## 00-COVER
REVIT TAG AUTOMATION GUIDE v4.3
ISO 19650 compliant ¦ STING Tools (C# / WPF) ¦ Paragraph engine + warning thresholds + BOQ automation + all-category coverage
KEY CHANGES v4.1 to v4.2
All-category gap analysis | 27 uncovered categories identified, mapped, and assigned paragraph containers. v4.1 covered 20 of 47.
Warning/threshold visibility | Standards-based range checking for 34 measurable parameters. Tag auto-appends warning text when value exceeds IEC/BS/UNBS/KCCA limits.
3-state paragraph engine | TAG_PARA_STATE_1/2/3_BOOL control compact/standard/comprehensive depth. if(<>"") gating for graceful degradation.
BOQ automation mapping | Natural-language BOQ descriptions from Revit schedule calculated values. Prefix/suffix token patterns for 8 BOQ bill types (Arch, Elec, Mech, HVAC, Fire, Plumbing, ICT, Lift).
New paragraph containers | 15 new discipline-specific containers added (Plumbing Fixtures, Conduits, Cable Trays, Curtain Panels, Stairs, Ramps, Furniture, Casework, Duct Accessories, Pipe Accessories, Communication/Data/Security/Telephone/Nurse Call Devices, Structural Foundations).
Material paragraph tags | 10 material paragraphs from v4.1 retained and cross-referenced.
BOQ template schedules | Standard Ugandan BOQ structure mapped to Revit schedule fields for Arch/Str and MEP templates.
v4.3 ¦ 20260301
v4.3 amendment (28-Feb-2026): Tag 7 paragraph engine supersedes 3-paragraph plan — all TAG 7 configurations unified into single sheet 07. Sheet 08: BOQ Automation Map merged & expanded. Sheet 09: PPDA BOQ Template Schedules (full Arch/Str/MEP). Sheet 03 updated: FUNC token confirmed in T1 source pool.
v4.3 amendment: Sheet 07 superseded with unified Tag 7 paragraph engine (3-paragraph plan DEPRECATED). Sheet 08 BOQ Template Schedules added — 9 bills, 35+ schedule definitions, full Uganda PPDA Arch/STR/MEP coverage. Date: 01-Mar-2026

## 01-CATEGORY-GAP-ANALYSIS
ALL-CATEGORY COVERAGE GAP ANALYSIS v4.2 ¦ 47 categories, 1030 parameters
Category | Discipline | v4.1 covered? | v4.1 tag container | v4.1 T7 paragraph | Total bindings | Useful params | Key param prefixes (discipline-specific) | v4.2 proposed T7 container | v4.2 formula source params | v4.2 paragraph template | BOQ bill mapping | Warning params available | Priority | Notes
TIER 1/2 — UNIVERSAL (covered v4.1)
Walls | ARCH | TRUE | ASS_TAG_1-6 | ARCH_TAG_7_PARA_WALL_TXT | 222 | 203 | BLE_WALL_(13), PER_THERM_(8), CST_S_(65) | — | — | — | Bill No.3 Arch | PER_THERM_U_VALUE, BLE_WALL_THICKNESS_MM | IMMEDIATE | Fully covered v4.1
Floors | ARCH | TRUE | ASS_TAG_1-6 | ARCH_TAG_7_PARA_FLOOR_TXT | 216 | 197 | BLE_FLR_(9), PER_THERM_(8), CST_S_(65) | — | — | — | Bill No.3 Arch | PER_THERM_U_VALUE, BLE_FLR_THICKNESS_MM | IMMEDIATE | Fully covered v4.1
Doors | ARCH | TRUE | ASS_TAG_1-6 | ARCH_TAG_7_PARA_DOOR_TXT | 294 | 275 | BLE_DOOR_(9), FLS_PROT_(3) | — | — | — | Bill No.3 Arch | BLE_DOOR_WIDTH_MM, FLS_PROT_FLS_RESISTANCE_RATING | IMMEDIATE | Fully covered v4.1
Windows | ARCH | TRUE | ASS_TAG_1-6 | ARCH_TAG_7_PARA_WIN_TXT | 296 | 277 | BLE_WINDOW_(8), PER_THERM_(8) | — | — | — | Bill No.3 Arch | BLE_WINDOW_U_VALUE, BLE_WINDOW_SOLAR_HEAT_GAIN | IMMEDIATE | Fully covered v4.1
Rooms | ARCH | TRUE | ASS_TAG_1-6 | ARCH_TAG_7_PARA_ROOM_TXT | 195 | 176 | BLE_ROOM_(2), ASS_ROOM_(3), ASS_DESIGN_(2) | — | — | — | N/A | ASS_DESIGN_LTG_LVL_LUX_NR, ASS_ROOM_AREA_SQ_M | IMMEDIATE | Fully covered v4.1
Ceilings | ARCH | TRUE | ASS_TAG_1-6 | MAT paragraphs | 214 | 195 | CST_S_(65), PER_THERM_(8), PER_ACOUSTICS_(6) | — | — | — | Bill No.3 Arch | PER_ACOUSTICS_BACKGROUND_NOISE_DB | HIGH | Material paragraphs only in v4.1
Roofs | ARCH | TRUE | ASS_TAG_1-6 | MAT paragraphs | 201 | 182 | CST_S_(65), PER_THERM_(8) | — | — | — | Bill No.3 Arch | PER_THERM_U_VALUE | HIGH | Material paragraphs only in v4.1
Structural Columns | STR | TRUE | ASS_TAG_1-6 | STR_TAG_7_PARA_COL_TXT | 64 | 51 | BLE_STRUCT_(13), CST_S_(29), STR_CONC_(1) | — | — | — | Bill No.3 Arch/Str | BLE_STRUCT_CONCRETE_GRADE_TXT | HIGH | Fully covered v4.1
Structural Framing | STR | TRUE | ASS_TAG_1-6 | STR_TAG_7_PARA_BEAM_TXT | 94 | 81 | BLE_STRUCT_(13), CST_S_(29), STR_STEEL_(1) | — | — | — | Bill No.3 Arch/Str | BLE_STRUCT_STEEL_GRADE_TXT | HIGH | Fully covered v4.1
Mechanical Equipment | HVAC | TRUE | HVC_EQP_TAG_01-03 | HVC_TAG_7_PARA_SPEC_TXT | 344 | 312 | HVC_CAP_(2), HVC_PWR_(1), HVC_EFF_(1), HVC_REFRIGERANT_(1) | — | — | — | Bill No.7 HVAC | HVC_CAP_KW, HVC_EFF_RATIO_NR, HVC_PWR_KW | IMMEDIATE | Fully covered v4.1
Ducts | HVAC | TRUE | HVC_DCT_TAG_01-02 | HVC_TAG_7_PARA_DUCT_TXT | 226 | 194 | HVC_DCT_(10), HVC_DUCT_(4) | — | — | — | Bill No.7 HVAC | HVC_DCT_FLW_CFM, HVC_VEL_MPS | IMMEDIATE | Fully covered v4.1
Duct Fittings | HVAC | TRUE | HVC_DCT_TAG_01-02 | HVC_TAG_7_PARA_DUCT_TXT | 226 | 194 | HVC_DCT_(10) | — | — | — | Bill No.7 HVAC | N/A (fittings counted) | IMMEDIATE | Shared with Ducts
Air Terminals | HVAC | TRUE | HVC_DCT_TAG_03 | HVC_TAG_7_PARA_AT_TXT | 328 | 296 | HVC_DCT_(10), HVC_TERMINAL_(4) | — | — | — | Bill No.7 HVAC | HVC_DCT_TERMINAL_SOUND_DB_NR | IMMEDIATE | Fully covered v4.1
Electrical Equipment | ELEC | TRUE | ELC_EQP_TAG_01-02 | ELC_TAG_7_PARA_PANEL_TXT | 359 | 327 | ELC_PNL_(11), ELC_CBL_(12), ELC_CKT_(8) | — | — | — | Bill No.4 Elec | ELC_PNL_CONNECTED_LOAD_KW, ELC_VLT_DROP_PCT | IMMEDIATE | Fully covered v4.1
Lighting Fixtures | ELEC | TRUE | LTG_FIX_TAG_01-02 | LTG_TAG_7_PARA_SPEC_TXT | 326 | 294 | LTG_FIX_(2), LTG_CLR_(2), LTG_EFFICACY_(1) | — | — | — | Bill No.4 Elec | LTG_FIX_LMP_WATTAGE_W, LTG_EFFICACY_LM_W | IMMEDIATE | Fully covered v4.1
Electrical Fixtures | ELEC | TRUE | ELE_FIX_TAG_1-2 | ELC_TAG_7_PARA_CIRCUIT_TXT | 340 | 308 | ELC_CKT_(8), ELC_CBL_(12) | — | — | — | Bill No.4 Elec | ELC_VLT_DROP_PCT | IMMEDIATE | Fully covered v4.1
Pipes | PLM | TRUE | PLM_EQP_TAG_01-02 | PLM_TAG_7_PARA_PIPE_TXT | 283 | 251 | PLM_PPE_(10), PLM_DRN_(24), PLM_VLV_(8) | — | — | — | Bill No.5 Mech | PLM_PPE_FLW_LPS, PLM_VEL_MPS | IMMEDIATE | Fully covered v4.1
Pipe Fittings | PLM | TRUE | PLM_EQP_TAG_01 | PLM_TAG_7_PARA_PIPE_TXT | 279 | 247 | PLM_PPE_(10) | — | — | — | Bill No.5 Mech | N/A (fittings counted) | IMMEDIATE | Shared with Pipes
Fire Alarm Devices | FLS | TRUE | FLS_DEV_TAG_01 | FLS_TAG_7_PARA_FA_TXT | 47 | 21 | FLS_SFTY_(11) | — | — | — | Bill No.4 Elec | FLS_SFTY_COVERAGE_AREA_SQ_M | IMMEDIATE | Fully covered v4.1
Sprinklers | FLS | TRUE | FLS_DEV_TAG_02 | FLS_TAG_7_PARA_SPR_TXT | 376 | 344 | FLS_SFTY_(11), FLS_PROT_(3) | — | — | — | Bill No.6 Fire | FLS_SFTY_TEMP_RATING_C, FLS_SFTY_FLW_RATE_LPM_NR | IMMEDIATE | Fully covered v4.1
CATEGORIES REQUIRING NEW v4.2 COVERAGE
Plumbing Fixtures | PLM | FALSE | ASS_TAG_1-6 only | NONE | 389 | 357 | PLM_DRN_(24), PLM_VLV_(8), PLM_PPE_(10), PLM_HOTWTR_(6) | PLM_TAG_7_PARA_FIXTURE_TXT | ASS_DESCRIPTION+PLM_PPE_MAT+PLM_PPE_SZ+PLM_DRN_BODY_MAT+ASS_MANUFACTURER+ASS_MODEL_NR | "This [DESC] fixture, [MAT] body, DN[SZ]. Drain: [DRN_MAT] with [TRAP]. By [MFR] model [MDL]." | Bill No.5 Mech | PLM_PPE_FLW_LPS, PLM_PSR_KPA | IMMEDIATE | HIGH-VALUE GAP: 357 useful params, sanitary fixtures in every BOQ
Plumbing Equipment | PLM | FALSE | ASS_TAG_1-6 only | NONE | 375 | 343 | PLM_DRN_(24), PLM_VLV_(8), PLM_HOTWTR_(6), PLM_PPE_(10) | PLM_TAG_7_PARA_EQUIPMENT_TXT | ASS_DESCRIPTION+PLM_PWR_KW+PLM_CAP_CU_M+PLM_HED_M+ASS_MANUFACTURER+ASS_MODEL_NR | "This [DESC], [CAP]m3 capacity, [PWR]kW, [HED]m head. By [MFR] model [MDL]." | Bill No.5 Mech | PLM_PWR_KW, PLM_HED_M, PLM_CAP_CU_M | IMMEDIATE | HIGH-VALUE GAP: pumps, tanks, heaters
Conduits | ELEC | FALSE | ASS_TAG_1-6 only | NONE | 333 | 301 | ELC_CDT_(6), ELC_CBL_(12), ELC_PNL_(9) | ELC_TAG_7_PARA_CONDUIT_TXT | ELC_CDT_SZ_MM+ELC_CDT_MAT+ELC_CDT_INSTALL_METHOD+ELC_CDT_CBL_FILL_PCT | "[SZ]mm [MAT] conduit, [METHOD] installation, [FILL]% cable fill." | Bill No.4 Elec | ELC_CDT_CBL_FILL_PCT | HIGH | Conduit fill >40% = warning
Conduit Fittings | ELEC | FALSE | NONE | NONE | 61 | 35 | ELC_CDT_(4), ELC_CBL_(12) | ELC_TAG_7_PARA_CONDUIT_TXT | (shared with Conduits) | (shared) | Bill No.4 Elec | N/A | MEDIUM | Counted, not described
Cable Trays | ELEC | FALSE | ELC_CTR_TAG_01 (T3 only) | NONE | 332 | 300 | ELC_CTR_(5), ELC_CBL_(12), ELC_PNL_(9) | ELC_TAG_7_PARA_TRAY_TXT | ELC_CTR_WIDTH_MM+ELC_CTR_DEPTH_MM+ELC_CTR_MAT+ELC_CTR_FILL_PCT | "[W]x[D]mm [MAT] cable tray, [FILL]% fill." | Bill No.4 Elec | ELC_CTR_FILL_PCT | HIGH | Tray fill >45% = warning
Cable Tray Fittings | ELEC | FALSE | NONE | NONE | 53 | 27 | ELC_CBL_(12) | ELC_TAG_7_PARA_TRAY_TXT | (shared with Cable Trays) | (shared) | Bill No.4 Elec | N/A | LOW | Counted only
Flex Ducts | HVAC | FALSE | HVC_FLX_TAG_01 (T3 only) | NONE | 224 | 192 | HVC_DCT_(8), HVC_DUCT_(4), HVC_TERMINAL_(4) | HVC_TAG_7_PARA_FLEXDUCT_TXT | HVC_DCT_MAT+HVC_DUCT_LINING+HVC_VEL_MPS | "Flexible [MAT] duct, [LINING] lining, [VEL]m/s." | Bill No.7 HVAC | HVC_VEL_MPS | HIGH | Flex duct velocity >6m/s = warning
Duct Accessories | HVAC | FALSE | HVC_DCT_ACC_TAG_01 (T3 only) | NONE | 226 | 194 | HVC_DCT_(10), HVC_DUCT_(4), HVC_TERMINAL_(4) | HVC_TAG_7_PARA_DCTACC_TXT | ASS_DESCRIPTION+HVC_DCT_MAT+HVC_CONTROL_TYPE+ASS_MANUFACTURER | "This [DESC] accessory, [MAT]. Control: [CTRL]. By [MFR]." | Bill No.7 HVAC | N/A | HIGH | Dampers, fire dampers, attenuators
Pipe Accessories | PLM | FALSE | ASS_TAG_1-6 only | NONE | 280 | 248 | PLM_VLV_(8), PLM_ACC_(3), PLM_STR_(4), PLM_EXJ_(6) | PLM_TAG_7_PARA_PIPEACC_TXT | ASS_DESCRIPTION+PLM_VLV_BODY_MAT+PLM_VLV_SZ+PLM_VLV_CV+PLM_PSR_KPA | "This [DESC], [MAT] body, DN[SZ], Cv [CV], PN[PSR]bar." | Bill No.5 Mech | PLM_PSR_KPA, PLM_VLV_CV_NR | HIGH | Valves, strainers, expansion joints
Curtain Panels | ARCH | FALSE | ASS_TAG_1-6 only | NONE | 211 | 192 | BLE_FACADE_(8), BLE_WALL_(13), CST_S_(68) | ARCH_TAG_7_PARA_FACADE_TXT | BLE_FACADE_CLR+BLE_FACADE_FINISH+BLE_FACADE_FIX_SYSTEM+BLE_FACADE_GLASS_TYPE+PER_THERM_U_VALUE | "[CLR] [FINISH] panel, [FIX] fixing, [GLASS]. U:[U]W/m2K." | Bill No.3 Arch | PER_THERM_U_VALUE_W_M2K_NR, BLE_FACADE_WTR_PENETRATION | HIGH | Facade panels + glazing
Curtain Wall Mullions | ARCH | FALSE | ASS_TAG_1-6 only | NONE | 180 | 174 | BLE_FACADE_(8), CST_S_(67) | ARCH_TAG_7_PARA_FACADE_TXT | (shared with Curtain Panels) | (shared) | Bill No.3 Arch | N/A | MEDIUM | Shared facade paragraph
Stairs | ARCH | FALSE | ASS_TAG_1-6 only | NONE | 189 | 170 | BLE_STAIR_(8), CST_S_(68) | ARCH_TAG_7_PARA_STAIR_TXT | BLE_STAIR_MAT+BLE_STAIR_RISE_MM+BLE_STAIR_GOING_MM+BLE_STAIR_WIDTH_MM+BLE_STAIR_TREAD_FINISH | "[MAT] stair, [RISE]mm rise, [GOING]mm going, [W]mm wide. Tread: [FINISH]. Handrail: [HR_MAT]." | Bill No.3 Arch | BLE_STAIR_RISE_MM, BLE_STAIR_GOING_MM, BLE_STAIR_WIDTH_MM | HIGH | Rise 150-180mm, going 250-300mm per BS 5395
Ramps | ARCH | FALSE | ASS_TAG_1-6 only | NONE | 188 | 169 | BLE_RAMP_(4), CST_S_(68) | ARCH_TAG_7_PARA_RAMP_TXT | BLE_RAMP_SLOPE_PCT+BLE_RAMP_SURFACE_FINISH+BLE_RAMP_HANDRAIL_BOTH_SIDES+RGL_ACCESS_CLEAR_WIDTH_MM | "Ramp at [SLOPE]% gradient, [FINISH] surface. Handrails: [HR]. Clear width: [W]mm." | N/A | BLE_RAMP_SLOPE_PCT, RGL_ACCESS_CLEAR_WIDTH_MM | HIGH | Slope max 1:12 per Uganda PWD Act 2020
Structural Foundations | STR | FALSE | ASS_TAG_1-6 only | NONE | 64 | 51 | BLE_STRUCT_(13), CST_S_(29) | STR_TAG_7_PARA_FDN_TXT | BLE_STRUCT_FOUNDATION_SZ+BLE_STRUCT_CONCRETE_GRADE+BLE_STRUCT_REINFORCEMENT | "[SZ] foundation, [GRADE] concrete, reinforcement: [REINF]." | Bill No.3 Arch/Str | BLE_STRUCT_CONCRETE_GRADE_TXT | HIGH | Foundation type + grade
Casework | ARCH | FALSE | ASS_TAG_1-6 only | NONE | 290 | 271 | CST_S_(65), ASS_(40+), FLS_SFTY_(11) | ARCH_TAG_7_PARA_CASEWORK_TXT | ASS_DESCRIPTION+ASS_MANUFACTURER+ASS_MODEL_NR+ASS_CST_TOTAL_UGX_NR+MAT_EPD_REF_TXT | "This [DESC]. By [MFR] model [MDL]. Material EPD: [EPD]." | Bill No.3 Arch | N/A | MEDIUM | Kitchen/lab casework, joinery
Furniture | ARCH | FALSE | ASS_TAG_1-6 only | NONE | 290 | 271 | CST_S_(65), ASS_(40+) | ARCH_TAG_7_PARA_FURNITURE_TXT | ASS_DESCRIPTION+ASS_MANUFACTURER+ASS_MODEL_NR+ASS_CST_TOTAL_UGX_NR | "This [DESC]. By [MFR] model [MDL]. [STATUS]." | N/A (FF&E schedule) | N/A | MEDIUM | FF&E schedule export
Specialty Equipment | MULTI | FALSE | ASS_TAG_1-6 only | NONE | 291 | 272 | CST_S_(65), ASS_(40+), FLS_SFTY_(11) | ASS_TAG_7_PARA_EQUIPMENT_TXT | ASS_DESCRIPTION+ASS_MANUFACTURER+ASS_MODEL_NR+ASS_EQUIPMENT_TAG+ASS_SYSTEM_TYPE | "This [DESC] ([SYS] system). By [MFR] model [MDL]. Tag: [TAG]." | Varies by type | N/A | MEDIUM | Lifts, generators, ATS, etc.
Communication Devices | ELEC/ICT | FALSE | COM_DEV_TAG_01 (T3 only) | NONE | 143 | 117 | COM_C_(7), ELC_CBL_(12), ELC_PNL_(11) | COM_TAG_7_PARA_BMS_TXT | COM_C_DEV_TYPE+COM_C_NETWORK_ADDRESS+COM_C_DEV_BACNET_INSTANCE+COM_C_DEV_CONTROLLER_NAME | "This [TYPE] device, network [NET], BACnet [ID]. Controller: [CTRL]." | Bill No.9 ICT | N/A | HIGH | BMS controllers, sensors
Data Devices | ELEC/ICT | FALSE | ICT_DEV_TAG_01 (T3 only) | NONE | 143 | 117 | ICT_(4), COM_C_(7), ELC_CBL_(12) | ICT_TAG_7_PARA_DATA_TXT | ICT_OUTLET_TYPE+ICT_PORT_NR+ICT_PATCH_PANEL+COM_C_DEV_TYPE | "[OUTLET] outlet, port [PORT], patch panel [PP]. Type: [TYPE]." | Bill No.9 ICT | N/A | MEDIUM | Structured cabling outlets
Telephone Devices | ELEC/ICT | FALSE | ICT_DEV_TAG_01 (T3 only) | NONE | 143 | 117 | ICT_(4), COM_C_(7), ELC_CBL_(12) | ICT_TAG_7_PARA_DATA_TXT | (shared with Data Devices) | (shared) | Bill No.9 ICT | N/A | MEDIUM | VoIP / analogue
Nurse Call Devices | ELEC/ICT | FALSE | NCL_DEV_TAG_01 (T3 only) | NONE | 142 | 116 | NCL_(3), COM_C_(7), ELC_CBL_(12) | NCL_TAG_7_PARA_NURSECALL_TXT | NCL_CALL_TYPE+NCL_ZONE+COM_C_DEV_TYPE+ASS_DESCRIPTION | "[CALL_TYPE] nurse call, zone [ZONE]. Type: [TYPE]." | Bill No.9 ICT | N/A | PROJECT | Healthcare only
Security Devices | ELEC/ICT | FALSE | SEC_DEV_TAG_01 (T3 only) | NONE | 142 | 116 | SEC_DEV_(2), SEC_CBL_(1), COM_C_(7), ELC_CBL_(12) | SEC_TAG_7_PARA_SECURITY_TXT | SEC_DEV_ZONE+SEC_CBL_NR+COM_C_DEV_TYPE+ASS_DESCRIPTION | "[TYPE] security device, zone [ZONE]. Cable: [CBL]." | Bill No.9 ICT | N/A | MEDIUM | CCTV, access control, intrusion
Lighting Devices | ELEC | FALSE | NONE | NONE | 32 | 6 | LTG_CLR_(2), LTG_FIX_(2), LTG_EFFICACY_(1) | LTG_TAG_7_PARA_SPEC_TXT | (shared with Lighting Fixtures) | (shared) | Bill No.4 Elec | LTG_FIX_LMP_WATTAGE_W | LOW | Sensors/controls, share LTG paragraph
EXCLUDED CATEGORIES (system/internal)
Generic Models | MULTI | TRUE | ASS_TAG_1-6 | N/A (too diverse) | 902 | 870 | All prefixes | N/A | N/A | N/A | N/A | N/A | N/A | Catch-all: use ASS_TAG_7_PARA_IDENTITY_TXT
Project Information | SYS | TRUE | TAG_STYLE_* | N/A | 41 | 0 | TAG_STYLE_(7), PRJ_(3) | N/A | N/A | N/A | N/A | N/A | N/A | Style control params only
Materials | SYS | TRUE | MAT_TAG_7_* | MAT paragraphs (10) | 105 | 90 | MAT_(46) | N/A | N/A | N/A | N/A | N/A | N/A | 10 material paragraphs in v4.1
Electrical Circuits | SYS | TRUE | N/A | N/A | 17 | 0 | ELC_CKT_(8) | N/A | N/A | N/A | N/A | N/A | N/A | System category, not taggable
SUMMARY | v4.1: 20 covered, v4.2: +27 = 47/47 (100%) | [6 empty] | 15 new paragraph containers + 3 shared

## 02-WARNING-THRESHOLDS
WARNING / THRESHOLD VISIBILITY SYSTEM v4.2 ¦ Standards-based range checking for Tag 7 paragraph engine
Mechanism: calculated value in Edit Label uses if(PARAM < MIN or PARAM > MAX, " [!WARNING: text]", "") appended to paragraph tier. STING Tools sets threshold params from project type.
Parameter | Category scope | Unit | Standard/code | Min threshold | Max threshold | Warning text (appended to tag) | Revit formula pattern | Severity | Notes
THERMAL PERFORMANCE
PER_THERM_U_VALUE_W_M2K_NR | Walls | W/m2K | Uganda NBC / ISO 6946 |  | 0.70 | [!U-VALUE EXCEEDS 0.70 W/m2K] | if(PER_THERM_U_VALUE_W_M2K_NR > 0.70, " [!U > 0.70]", "") | HIGH | Tropical climate: external walls. Internal walls exempt.
PER_THERM_U_VALUE_W_M2K_NR | Roofs | W/m2K | Uganda NBC |  | 0.50 | [!U-VALUE EXCEEDS 0.50 W/m2K] | if(PER_THERM_U_VALUE_W_M2K_NR > 0.50, " [!U > 0.50]", "") | HIGH | Roof U-value more restrictive than walls
PER_THERM_U_VALUE_W_M2K_NR | Floors | W/m2K | Uganda NBC |  | 0.70 | [!U-VALUE EXCEEDS 0.70 W/m2K] | if(PER_THERM_U_VALUE_W_M2K_NR > 0.70, " [!U > 0.70]", "") | MEDIUM | Ground floors / suspended
BLE_WINDOW_U_VALUE_W_M_2K_NR | Windows | W/m2K | IEC / ASHRAE 90.1 |  | 3.00 | [!WINDOW U > 3.00 W/m2K] | if(BLE_WINDOW_U_VALUE_W_M_2K_NR > 3.00, " [!U > 3.00]", "") | HIGH | Tropical: less strict than temperate
BLE_WINDOW_SOLAR_HEAT_GAIN_COEFFICIENT_NR | Windows | ratio | ASHRAE 90.1 tropical |  | 0.40 | [!SHGC EXCEEDS 0.40] | if(BLE_WINDOW_SOLAR_HEAT_GAIN_COEFFICIENT_NR > 0.40, " [!SHGC > 0.40]", "") | HIGH | East/West facades critical
ELECTRICAL
ELC_VLT_DROP_PCT | Electrical Equipment, Electrical Fixtures | % | IEC 60364-5-52 / BS 7671 |  | 4.0 | [!VD EXCEEDS 4%] | if(ELC_VLT_DROP_PCT > 4.0, " [!VD > 4%]", "") | CRITICAL | Final circuit limit. Submain: 2.5%.
ELC_CDT_CBL_FILL_PCT | Conduits | % | IEC 60364 / BS 7671 |  | 40 | [!CONDUIT FILL > 40%] | if(ELC_CDT_CBL_FILL_PCT > 40, " [!FILL > 40%]", "") | HIGH | 40% for 3+ cables
ELC_CTR_FILL_PCT | Cable Trays | % | IEC 61537 |  | 45 | [!TRAY FILL > 45%] | if(ELC_CTR_FILL_PCT > 45, " [!FILL > 45%]", "") | HIGH | Power cables. Data: 50% OK.
ELC_PNL_CONNECTED_LOAD_KW | Electrical Equipment | kW | Design practice |  | (80% of panel rating) | [!LOAD > 80% PANEL CAPACITY] | if(ELC_PNL_CONNECTED_LOAD_KW > ELC_PNL_RATED_KW * 0.8, " [!OVERLOADED]", "") | CRITICAL | Needs ELC_PNL_RATED_KW param (new)
ELC_PNL_SHORT_CIRCUIT_KA | Electrical Equipment | kA | IEC 60947-2 | 6 |  | [!FAULT LEVEL < 6kA] | if(ELC_PNL_SHORT_CIRCUIT_KA < 6, " [!SC < 6kA]", "") | MEDIUM | Minimum for MCBs
PLUMBING / DRAINAGE
PLM_PPE_FLW_LPS | Pipes (hot water) | L/s | BS EN 806-3 |  | 2.0 | [!FLOW > 2.0 L/s] | if(PLM_PPE_FLW_LPS > 2.0, " [!FLOW > 2.0]", "") | MEDIUM | HW recirculation limit
PLM_VEL_MPS | Pipes | m/s | BS EN 806-3 / CIBSE |  | 2.0 | [!VELOCITY > 2.0 m/s] | if(PLM_VEL_MPS > 2.0, " [!VEL > 2.0]", "") | HIGH | Noise threshold. >3.0 = erosion.
PLM_PSR_KPA | Pipes, Plumbing Equipment | kPa | NWSC supply | 150 | 600 | [!PRESSURE OUT OF RANGE] | if(or(PLM_PSR_KPA < 150, PLM_PSR_KPA > 600), " [!PSR]", "") | MEDIUM | NWSC typical 150-400 kPa
HVAC
HVC_VEL_MPS | Ducts (supply) | m/s | CIBSE Guide B / ASHRAE |  | 6.0 | [!DUCT VEL > 6.0 m/s] | if(HVC_VEL_MPS > 6.0, " [!VEL > 6.0]", "") | HIGH | Main duct. Branch: 4.0 m/s.
HVC_VEL_MPS | Flex Ducts | m/s | SMACNA |  | 4.0 | [!FLEX VEL > 4.0 m/s] | if(HVC_VEL_MPS > 4.0, " [!VEL > 4.0]", "") | HIGH | Flex ducts more restrictive
HVC_DCT_TERMINAL_SOUND_DB_NR | Air Terminals | dB(A) | CIBSE Guide A |  | 35 | [!TERMINAL NOISE > 35 dB] | if(HVC_DCT_TERMINAL_SOUND_DB_NR > 35, " [!NOISE > 35dB]", "") | MEDIUM | Office/meeting rooms. Plant: 45 dB OK.
HVC_EFF_RATIO_NR | Mechanical Equipment | COP/EER | ASHRAE 90.1 | 3.0 |  | [!EFFICIENCY < 3.0 COP] | if(HVC_EFF_RATIO_NR < 3.0, " [!EFF < 3.0]", "") | HIGH | VRF: expect 3.5+. Split: 3.0 min.
FIRE LIFE SAFETY
FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN | Walls, Doors, Floors | min | BS 9999 / Uganda NBC | 30 |  | [!FIRE RATING < 30 MIN] | if(FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN < 30, " [!FRR < 30]", "") | CRITICAL | Compartment walls. Escape: 60 min.
FLS_SFTY_TEMP_RATING_C | Sprinklers | degC | BS EN 12845 | 57 | 79 | [!SPRINKLER TEMP OUT OF RANGE] | if(or(FLS_SFTY_TEMP_RATING_C < 57, FLS_SFTY_TEMP_RATING_C > 79), " [!TEMP]", "") | HIGH | Ordinary hazard: 68C typical
FLS_SFTY_COVERAGE_AREA_SQ_M | Sprinklers, Fire Alarm Devices | m2 | BS EN 12845 / BS 5839 |  | 21 | [!COVERAGE > 21 m2] | if(FLS_SFTY_COVERAGE_AREA_SQ_M > 21, " [!AREA > 21]", "") | HIGH | Ordinary hazard max 21m2/head
ACCESSIBILITY (Uganda PWD Act 2020)
BLE_RAMP_SLOPE_PCT | Ramps | % | Uganda PWD Act 2020 |  | 8.33 | [!RAMP SLOPE > 1:12 (8.33%)] | if(BLE_RAMP_SLOPE_PCT > 8.33, " [!SLOPE > 1:12]", "") | CRITICAL | Max 1:12 gradient, 9m max run
RGL_ACCESS_CLEAR_WIDTH_MM | Doors, Ramps, Corridors | mm | Uganda PWD Act 2020 | 900 |  | [!CLEAR WIDTH < 900mm] | if(RGL_ACCESS_CLEAR_WIDTH_MM < 900, " [!WIDTH < 900]", "") | CRITICAL | Wheelchair access minimum
BLE_DOOR_WIDTH_MM | Doors | mm | Uganda PWD Act 2020 | 900 |  | [!DOOR WIDTH < 900mm] | if(BLE_DOOR_WIDTH_MM < 900, " [!DOOR < 900mm]", "") | CRITICAL | Accessible route doors
STAIRS (BS 5395)
BLE_STAIR_RISE_MM | Stairs | mm | BS 5395-1 | 150 | 190 | [!RISE OUT OF RANGE] | if(or(BLE_STAIR_RISE_MM < 150, BLE_STAIR_RISE_MM > 190), " [!RISE]", "") | HIGH | Private: 150-220. Public: 150-190.
BLE_STAIR_GOING_MM | Stairs | mm | BS 5395-1 | 250 | 400 | [!GOING OUT OF RANGE] | if(or(BLE_STAIR_GOING_MM < 250, BLE_STAIR_GOING_MM > 400), " [!GOING]", "") | HIGH | Public stair: 250-400mm
BLE_STAIR_WIDTH_MM | Stairs (escape) | mm | BS 9999 / Uganda NBC | 1000 |  | [!STAIR WIDTH < 1000mm] | if(BLE_STAIR_WIDTH_MM < 1000, " [!WIDTH < 1000]", "") | CRITICAL | Escape stair min 1000mm
ACOUSTIC
PER_ACOUSTICS_BACKGROUND_NOISE_DB | Rooms (offices) | dB(A) | CIBSE Guide A / BB93 |  | 40 | [!BACKGROUND NOISE > 40 dB] | if(PER_ACOUSTICS_BACKGROUND_NOISE_DB > 40, " [!NOISE > 40dB]", "") | MEDIUM | Open office: 40. Private: 35.
ASS_DESIGN_LTG_LVL_LUX_NR | Rooms (offices) | lux | BS EN 12464-1 / CIBSE | 300 |  | [!ILLUMINANCE < 300 lux] | if(ASS_DESIGN_LTG_LVL_LUX_NR < 300, " [!LUX < 300]", "") | MEDIUM | General office: 300-500 lux
STRUCTURAL
BLE_STRUCT_CONCRETE_GRADE_TXT | Str Columns, Str Framing, Str Foundations | grade | BS 8500 / UNBS |  |  | [!CHECK GRADE vs EXPOSURE] | (text comparison via lookup table) | HIGH | C25/30 min for reinforced. C30/37 for water-retaining.
SUSTAINABILITY / ENVIRONMENT
PER_SUST_CARBON_FOOTPRINT_KG | Walls, Floors, Roofs | kgCO2e/m2 | EDGE / IFC Performance |  | (varies by element) | [!EMBODIED CARBON HIGH] | if(PER_SUST_CARBON_FOOTPRINT_KG > THRESHOLD, " [!CO2]", "") | MEDIUM | EDGE benchmark varies by type

## 03-TAG-CONTAINER-ARCH
TAG CONTAINER ARCHITECTURE v4.2 ¦ All 47 categories covered ¦ Paragraph engine + warning thresholds
TIER 1 | Universal (all 47+4 categories) — max 1 line per tag
TIER 2 | System identity (MEP) — max 2 lines per tag
TIER 3 | Discipline specialist — max 2 lines (3 for info-dense: DB panels, HVAC eqp, lighting)
TAG 7 | Paragraph description — 3-state depth: compact (S1) / standard (S2) / comprehensive (S3)
TAG 7W | Warning append — auto-appended when threshold exceeded. Red label text.
SUB (.1) | Additional physical tag line from v3.1
v4.2 NEW | New container or warning for v4.2
Tier | Sub-tier / tag line | Parameter name | Phys. tag pos. | Category scope | Formula / content | Key source params (verified) | Tag family | Lines | Max display | New? | Warning integration | Notes | Priority
TIER 1 — UNIVERSAL ¦ All 47+4 categories ¦ Max 1 line
T1 | Full tag | ASS_TAG_1_TXT | Line 1 | All 53 | DISC-LOC-ZONE-LVL-SYS-FUNC-PROD-NUM | 8 source tokens | PRJ_ISO_Tag.rfa | 1 | 1 | No | — | Primary identity | IMMEDIATE
T1 | Short tag | ASS_TAG_4_TXT | Line 1 | All 53 | [PROD]-[NUM] | ASS_PRODCT_COD_TXT, ASS_SEQ_NUM_TXT | Short_Tag.rfa | 1 | 1 | No | — | Congested views | IMMEDIATE
T1 | With description | ASS_TAG_5_TXT | Line 1+2 | All 53 | [PROD]-[NUM] + description | PRODCT+SEQ+ASS_DESCRIPTION_TXT | Desc_Tag.rfa | 2 | 1 | No | — | Tag 5 | IMMEDIATE
T1 | Status / comments | ASS_TAG_6_TXT | Line 1+2 | All 53 | [PROD]-[NUM] + status + comments | PRODCT+SEQ+ASS_STATUS_TXT+PRJ_COMMENTS_TXT | Status_Tag.rfa | 2 | 1 | No | — | Snagging | IMMEDIATE
TIER 2 — SYSTEM IDENTITY ¦ MEP categories ¦ Max 2 lines
T2 | System ID | ASS_TAG_2_TXT | Line 1 | All MEP | [SYS]-[FUNC]-[PROD]-[NUM] | ASS_SYSTEM_TYPE_TXT+ASS_FUNC_TXT+PRODCT+SEQ | MEP_Sys_Tag.rfa | 1 | 2 | No | — | Omits spatial tokens | IMMEDIATE
T2 | Install data | ASS_TAG_3_TXT | Line 2 | All MEP | COE:FFL+[HGT]mm [MNT] Dtl:[DTL] | MNT_HGT_MM+MNT_TYPE_TXT+ASS_INST_DETAIL_NUM_TXT | MEP_Sys_Tag.rfa | 2 | 2 | No | — | Height / detail ref | IMMEDIATE
TAG 7 — NEW v4.2 PARAGRAPH CONTAINERS ¦ Gap categories
T7-P | Plumb fixture para | PLM_TAG_7_PARA_FIXTURE_TXT | Para | Plumbing Fixtures | "This [DESC] fixture, [MAT] body, DN[SZ]. Drain: [DRN_MAT] with [TRAP]. By [MFR] model [MDL]." | ASS_DESCRIPTION+PLM_PPE_MAT+PLM_PPE_SZ+PLM_DRN_BODY_MAT+ASS_MANUFACTURER+ASS_MODEL_NR | PLM_Fix_Para.rfa | para | 2 | v4.2 NEW | PLM_PPE_FLW_LPS > 0.15 | Sanitary fittings: WC, WHB, urinal, sink | IMMEDIATE
T7-P | Plumb equip para | PLM_TAG_7_PARA_EQUIPMENT_TXT | Para | Plumbing Equipment | "This [DESC], [CAP]m3 capacity, [PWR]kW, [HED]m head. By [MFR] model [MDL]." | ASS_DESCRIPTION+PLM_PWR_KW+PLM_CAP_CU_M+PLM_HED_M+ASS_MANUFACTURER+ASS_MODEL_NR | PLM_Eqp_Para.rfa | para | 2 | v4.2 NEW | PLM_PWR_KW, PLM_HED_M | Pumps, tanks, heaters | IMMEDIATE
T7-P | Pipe accessory para | PLM_TAG_7_PARA_PIPEACC_TXT | Para | Pipe Accessories | "This [DESC], [MAT] body, DN[SZ], Cv [CV], PN[PSR]bar." | ASS_DESCRIPTION+PLM_VLV_BODY_MAT+PLM_VLV_SZ+PLM_VLV_CV+PLM_PSR_KPA | PLM_Acc_Para.rfa | para | 2 | v4.2 NEW | PLM_PSR_KPA | Valves, strainers, exp joints | HIGH
T7-E | Conduit para | ELC_TAG_7_PARA_CONDUIT_TXT | Para | Conduits, Conduit Fittings | "[SZ]mm [MAT] conduit, [METHOD] installation, [FILL]% cable fill." | ELC_CDT_SZ_MM+ELC_CDT_MAT+ELC_CDT_INSTALL_METHOD+ELC_CDT_CBL_FILL_PCT | ELC_Cdt_Para.rfa | para | 2 | v4.2 NEW | ELC_CDT_CBL_FILL_PCT > 40% | Fill warning at 40% | HIGH
T7-E | Cable tray para | ELC_TAG_7_PARA_TRAY_TXT | Para | Cable Trays, Cable Tray Fittings | "[W]x[D]mm [MAT] cable tray, [FILL]% fill." | ELC_CTR_WIDTH_MM+ELC_CTR_DEPTH_MM+ELC_CTR_MAT+ELC_CTR_FILL_PCT | ELC_CT_Para.rfa | para | 2 | v4.2 NEW | ELC_CTR_FILL_PCT > 45% | Fill warning at 45% | HIGH
T7-H | Flex duct para | HVC_TAG_7_PARA_FLEXDUCT_TXT | Para | Flex Ducts | "Flexible [MAT] duct, [LINING] lining, [VEL]m/s." | HVC_DCT_MAT+HVC_DUCT_LINING+HVC_VEL_MPS | HVAC_FlxDuct_Para.rfa | para | 2 | v4.2 NEW | HVC_VEL_MPS > 4.0 | Flex velocity limit lower | HIGH
T7-H | Duct accessory para | HVC_TAG_7_PARA_DCTACC_TXT | Para | Duct Accessories | "This [DESC] accessory, [MAT]. Control: [CTRL]. By [MFR]." | ASS_DESCRIPTION+HVC_DCT_MAT+HVC_CONTROL_TYPE+ASS_MANUFACTURER | HVAC_DctAcc_Para.rfa | para | 2 | v4.2 NEW | — | Dampers, fire dampers | HIGH
T7-A | Curtain/facade para | ARCH_TAG_7_PARA_FACADE_TXT | Para | Curtain Panels, Curtain Wall Mullions | "[CLR] [FINISH] panel, [FIX] fixing, [GLASS]. U:[U]W/m2K." | BLE_FACADE_CLR+FINISH+FIX_SYSTEM+GLASS_TYPE+PER_THERM_U_VALUE | ARCH_Facade_Para.rfa | para | 2 | v4.2 NEW | PER_THERM_U_VALUE > 2.20 | Curtain wall U-value | HIGH
T7-A | Stair para | ARCH_TAG_7_PARA_STAIR_TXT | Para | Stairs | "[MAT] stair, [RISE]mm rise, [GOING]mm going, [W]mm wide. Tread: [FINISH]." | BLE_STAIR_MAT+RISE_MM+GOING_MM+WIDTH_MM+TREAD_FINISH+HANDRAIL_MAT | ARCH_Stair_Para.rfa | para | 2 | v4.2 NEW | RISE 150-190, GOING 250-400, WIDTH >= 1000 | BS 5395 + BS 9999 thresholds | HIGH
T7-A | Ramp para | ARCH_TAG_7_PARA_RAMP_TXT | Para | Ramps | "Ramp at [SLOPE]% gradient, [FINISH] surface. Handrails: [HR]. Clear width: [W]mm." | BLE_RAMP_SLOPE_PCT+SURFACE_FINISH+HANDRAIL_BOTH_SIDES+RGL_ACCESS_CLEAR_WIDTH_MM | ARCH_Ramp_Para.rfa | para | 2 | v4.2 NEW | SLOPE > 8.33%, WIDTH < 900mm | Uganda PWD Act 2020 | HIGH
T7-S | Foundation para | STR_TAG_7_PARA_FDN_TXT | Para | Structural Foundations | "[SZ] foundation, [GRADE] concrete, reinforcement: [REINF]." | BLE_STRUCT_FOUNDATION_SZ+CONCRETE_GRADE+REINFORCEMENT | STR_Fdn_Para.rfa | para | 2 | v4.2 NEW | Concrete grade check | Foundation spec | HIGH
T7-A | Casework para | ARCH_TAG_7_PARA_CASEWORK_TXT | Para | Casework | "This [DESC]. By [MFR] model [MDL]. Material EPD: [EPD]." | ASS_DESCRIPTION+ASS_MANUFACTURER+ASS_MODEL_NR+MAT_EPD_REF_TXT | ARCH_Case_Para.rfa | para | 2 | v4.2 NEW | — | Kitchen/lab casework | MEDIUM
T7-A | Furniture para | ARCH_TAG_7_PARA_FURNITURE_TXT | Para | Furniture | "This [DESC]. By [MFR] model [MDL]. [STATUS]." | ASS_DESCRIPTION+ASS_MANUFACTURER+ASS_MODEL_NR+ASS_STATUS_TXT | ARCH_Furn_Para.rfa | para | 2 | v4.2 NEW | — | FF&E | MEDIUM
T7 | Specialty equip para | ASS_TAG_7_PARA_EQUIPMENT_TXT | Para | Specialty Equipment | "This [DESC] ([SYS] system). By [MFR] model [MDL]. Tag: [TAG]." | ASS_DESCRIPTION+ASS_SYSTEM_TYPE+ASS_MANUFACTURER+ASS_MODEL_NR+ASS_EQUIPMENT_TAG | ASS_Eqp_Para.rfa | para | 2 | v4.2 NEW | — | Lifts, generators, etc. | MEDIUM
T7-E | BMS device para | COM_TAG_7_PARA_BMS_TXT | Para | Communication Devices | "This [TYPE] device, network [NET], BACnet [ID]. Controller: [CTRL]." | COM_C_DEV_TYPE+NETWORK_ADDRESS+BACNET_INSTANCE+CONTROLLER_NAME | COM_Para.rfa | para | 2 | v4.2 NEW | — | BMS controllers | HIGH
T7-E | Data outlet para | ICT_TAG_7_PARA_DATA_TXT | Para | Data Devices, Telephone Devices | "[OUTLET] outlet, port [PORT], patch panel [PP]." | ICT_OUTLET_TYPE+ICT_PORT_NR+ICT_PATCH_PANEL | ICT_Para.rfa | para | 1 | v4.2 NEW | — | Structured cabling | MEDIUM
T7-E | Nurse call para | NCL_TAG_7_PARA_NURSECALL_TXT | Para | Nurse Call Devices | "[CALL_TYPE] nurse call, zone [ZONE]." | NCL_CALL_TYPE+NCL_ZONE+COM_C_DEV_TYPE | NCL_Para.rfa | para | 1 | v4.2 NEW | — | Healthcare only | PROJECT
T7-E | Security para | SEC_TAG_7_PARA_SECURITY_TXT | Para | Security Devices | "[TYPE] security device, zone [ZONE]. Cable: [CBL]." | SEC_DEV_ZONE+SEC_CBL_NR+COM_C_DEV_TYPE+ASS_DESCRIPTION | SEC_Para.rfa | para | 1 | v4.2 NEW | — | CCTV, access, intrusion | MEDIUM

## 04-BOQ-AUTOMATION-MAP
BOQ AUTOMATION MAP v4.2 ¦ Natural-language BOQ descriptions assembled from Revit parameters using schedule calculated values
Pattern: schedule calculated value = PREFIX + if(PARAM<>"", PARAM, "TBC") + SUFFIX. Assembles full BOQ item description without labels. Exported to Excel for QS pricing.
BOQ bill | BOQ element/section | Revit category | BOQ description pattern (natural language) | Revit params -> tokens | Prefix text | Suffix text | Unit param | Qty source | Schedule name | Notes | BOQ_DESC_FORMULA — Complete Revit Calculated Value (paste into Edit Label)
BILL No.4 — ELECTRICAL INSTALLATIONS
Bill 4 | Lighting points | Electrical Fixtures | Lighting points wired by [CBL_TYPE] copper cables in [CDT_SZ]mm heavy gauge PVC conduit [METHOD] complete with [MFR] steel boxes and all accessories. | ELC_CKT_CBL_TYPE_TXT, ELC_CDT_SZ_MM, ELC_CDT_INSTALL_METHOD_TXT, ASS_MANUFACTURER_TXT | Lighting points wired by | complete with steel boxes and all accessories. | NO | Count | BOQ-ELC-Lighting-Points | Per floor element grouping | "Lighting points wired by " + if(ELC_CKT_CBL_TYPE_TXT<>"",ELC_CKT_CBL_TYPE_TXT,"3x1.5mm² SC PVC") + " copper cables in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " heavy gauge PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"concealed") + " conduit complete with " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"MK") + " steel boxes and all accessories."
Bill 4 | Socket outlet points | Electrical Fixtures | Socket outlet points wired as a ring by [CBL_TYPE] copper cables in [CDT_SZ]mm heavy gauge PVC [METHOD] conduit/trunking complete with boxes for sockets on trunking and all accessories. | ELC_CKT_CBL_TYPE_TXT, ELC_CDT_SZ_MM, ELC_CDT_INSTALL_METHOD_TXT | Socket outlet points wired as a ring by | complete with all accessories. | NO | Count | BOQ-ELC-Socket-Points | Ring/radial from circuit type | "Socket outlet points wired as a ring by " + if(ELC_CKT_CBL_TYPE_TXT<>"",ELC_CKT_CBL_TYPE_TXT,"3x2.5mm² SC PVC") + " copper cables in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " heavy gauge PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"concealed") + " conduit/trunking complete with all accessories."
Bill 4 | Lighting fittings | Lighting Fixtures | [TYPE] [WATT]W LED [MOUNTING], [SIZE], with [CTRL] interface as [MFR] or equal approved. (Light Type [CODE]) | LTG_FIX_TYPE_CLASSIFICATION_TXT, LTG_FIX_LMP_WATTAGE_W, ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT |  | or equal approved. | NO | Count | BOQ-ELC-Luminaires | Group by type mark | if(LTG_FIX_TYPE_CLASSIFICATION_TXT<>"",LTG_FIX_TYPE_CLASSIFICATION_TXT,"") + " " + if(LTG_FIX_LMP_WATTAGE_W<>"",LTG_FIX_LMP_WATTAGE_W+"W ","") + "LED luminaire " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"") + " as " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"approved mfr") + " or equal approved."
Bill 4 | Light switches | Electrical Fixtures | [RATING]A [GANGS] gang [WAYS] way light switch as [MFR] or equal approved complete with all accessories. | ELC_CKT_BRK_RATING_A, ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT |  | complete with all accessories. | NO | Count | BOQ-ELC-Switches |  | if(ELC_CKT_BRK_RATING_A<>"",ELC_CKT_BRK_RATING_A+"A ","10A ") + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"1 gang 1 way ") + "light switch as " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"MK or equal") + " complete with all accessories."
Bill 4 | Sockets | Electrical Fixtures | [RATING]A [POLES]pin [CONFIG] switched socket outlets on wall/trunking as [MFR] or equal approved. | ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT |  |  | NO | Count | BOQ-ELC-Sockets | Twin/single from type | if(ELC_CKT_BRK_RATING_A<>"",ELC_CKT_BRK_RATING_A+"A ","13A ") + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"3-pin double ") + "switched socket outlet " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"MK or equal") + " or equal approved."
Bill 4 | Cable trays | Cable Trays | Steel cable tray [WIDTH]x[DEPTH]mm fixed in cable duct complete with all accessories. | ELC_CTR_WIDTH_MM, ELC_CTR_DEPTH_MM, ELC_CTR_MAT_TXT | Steel cable tray | complete with all accessories. | LM | Length | BOQ-ELC-CableTrays | Total length per size | "Steel cable tray " + if(ELC_CTR_WIDTH_MM<>"",ELC_CTR_WIDTH_MM,"100") + "x" + if(ELC_CTR_DEPTH_MM<>"",ELC_CTR_DEPTH_MM,"50") + "mm complete with all fittings and accessories."
Bill 4 | Conduits | Conduits | [CDT_SZ]mm [CDT_MAT] conduit [METHOD] complete with all accessories. | ELC_CDT_SZ_MM, ELC_CDT_MAT_TXT, ELC_CDT_INSTALL_METHOD_TXT |  | complete with all accessories. | LM | Length | BOQ-ELC-Conduits | Group by size+material | if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " heavy gauge PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"concealed") + " conduit complete with all accessories." + if(ELC_CDT_CBL_FILL_PCT>40," [!FILL>40%]","")
Bill 4 | DB panels | Electrical Equipment | [DESIGNATION] distribution board, [VLT]V [PHS]-phase, [WAYS] ways, [MAIN]A main breaker, [SC]kA fault level, complete with all MCBs, RCDs and accessories. | ELC_PNL_DESIGNATION_NAME_TXT, ELC_PNL_VLT_V, ELC_PNL_PHS_COUNT_NR, ELC_PNL_NUM_OF_WAYS_NR, ELC_PNL_MAIN_BRK_A, ELC_PNL_SHORT_CIRCUIT_KA |  | complete with all MCBs, RCDs and accessories. | NO | Count | BOQ-ELC-DBPanels | 1 per panel | if(ELC_PNL_DESIGNATION_NAME_TXT<>"",ELC_PNL_DESIGNATION_NAME_TXT,"DB") + " distribution board, " + if(ELC_PNL_VLT_V<>"",ELC_PNL_VLT_V+"V ","230V ") + if(ELC_PNL_PHS_COUNT_NR<>"",ELC_PNL_PHS_COUNT_NR+"-phase, ","1-phase, ") + if(ELC_PNL_NUM_OF_WAYS_NR<>"",ELC_PNL_NUM_OF_WAYS_NR+" ways, ","? ways, ") + if(ELC_PNL_MAIN_BRK_A<>"",ELC_PNL_MAIN_BRK_A+"A main, ","?A main, ") + if(ELC_PNL_SHORT_CIRCUIT_KA<>"",ELC_PNL_SHORT_CIRCUIT_KA+"kA fault, ","") + "complete with all MCBs, RCDs and accessories." + if(ELC_PNL_CONNECTED_LOAD_KW>ELC_PNL_RATED_KW*0.8," [!OVERLOADED]","") + if(ELC_PNL_SHORT_CIRCUIT_KA<6," [!SC<6kA]","")
Bill 4 | Fire alarm points | Fire Alarm Devices | Fire alarm [TYPE] points in [CDT_SZ]mm heavy gauge PVC [METHOD] conduit complete with all accessories. | FLS_SFTY_DEV_TYPE_TXT, ELC_CDT_SZ_MM, ELC_CDT_INSTALL_METHOD_TXT | Fire alarm | complete with all accessories. | NO | Count | BOQ-ELC-FireAlarm | Detectors, MCPs, sounders | "Fire alarm " + if(FLS_SFTY_DEV_TYPE_TXT<>"",FLS_SFTY_DEV_TYPE_TXT,"detector") + " in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","20mm") + " PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"concealed") + " conduit complete with all accessories."
Bill 4 | CCTV / security | Security Devices | [TYPE] points in [CDT_SZ]mm heavy gauge PVC concealed conduit/trunking complete with all accessories. | SEC_DEV_TYPE_TXT, ELC_CDT_SZ_MM |  | complete with all accessories. | NO | Count | BOQ-ELC-Security | CCTV, access control | "CCTV " + if(SEC_DEV_TYPE_TXT<>"",SEC_DEV_TYPE_TXT,"dome camera") + " in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " PVC concealed conduit, " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"Hikvision or equal") + " complete with bracket and accessories."
BILL No.5 — MECHANICAL INSTALLATIONS
Bill 5 | Sanitary fittings (WC) | Plumbing Fixtures | [MFR_DESC] WC pan [TYPE], [COLOUR] colour, vitreous china to BS3402 with [OUTLET] outlet complete with flush valve, seat and cover and all accessories. | ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT, ASS_MODEL_NR_TXT |  | and all accessories. | NO | Count | BOQ-PLM-SanitaryWC | Group by type mark | if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"Armitage Shanks or equal") + " WC pan " + if(ASS_MODEL_NR_TXT<>"",ASS_MODEL_NR_TXT,"") + ", " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"white vitreous china") + ", complete with close coupled cistern, soft close seat and cover and all accessories."
Bill 5 | Sanitary fittings (WHB) | Plumbing Fixtures | [DIM] countertop vitreous china wash hand basin, with [TAPS] tap hole [WASTE] chrome plated waste, plastic bottle trap, complete with all accessories as [MFR] or equal approved. | ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT |  | or equal approved. | NO | Count | BOQ-PLM-SanitaryWHB |  | if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"600mm WHB") + " wash hand basin, " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"or equal") + " complete with mixer tap, waste, trap and all accessories."
Bill 5 | PPR pipework | Pipes | [SZ]mm PPR pipe work [PN_RATING] complete with fittings. | PLM_PPE_SZ_MM, PLM_PPE_PSR_RATING_BAR, PLM_PPE_MAT_TXT |  | complete with fittings. | LM | Length | BOQ-PLM-Pipework | Group by size + material | if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + if(PLM_PPE_MAT_TXT<>"",PLM_PPE_MAT_TXT+" ","PPR ") + "pipe " + if(PLM_PPE_PSR_RATING_BAR<>"",PLM_PPE_PSR_RATING_BAR+" bar rated ","") + "complete with fittings." + if(PLM_VEL_MPS>2.0," [!VEL>2.0]","") + if(or(PLM_PSR_KPA<150,PLM_PSR_KPA>600)," [!PSR]","")
Bill 5 | Globe valves | Pipe Accessories | [SZ]mm globe valves. | PLM_VLV_SZ_NR |  |  | NO | Count | BOQ-PLM-Valves | Group by size + type | if(PLM_VLV_SZ_NR<>"",PLM_VLV_SZ_NR+"mm ","") + if(PLM_VLV_TYPE_TXT<>"",PLM_VLV_TYPE_TXT,"globe valve") + "."
Bill 5 | Drainage pipework | Pipes (drainage system) | [SZ]mm PVC soil waste pipe on wall and/or in duct. | PLM_PPE_SZ_MM, PLM_PPE_MAT_TXT |  |  | LM | Length | BOQ-PLM-Drainage | System type = drainage filter | if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + if(PLM_DRN_BODY_MAT_TXT<>"",PLM_DRN_BODY_MAT_TXT+" ","uPVC ") + "drainage pipe complete with fittings."
Bill 5 | Water heaters | Plumbing Equipment | Pressure type under sink water heater [CAP]litres with glass lining complete with all accessories as [MFR] or equal approved. | PLM_CAP_CU_M, ASS_MANUFACTURER_TXT |  | or equal approved. | NO | Count | BOQ-PLM-WaterHeater |  | if(PLM_HOTWTR_CAPACITY_L<>"",PLM_HOTWTR_CAPACITY_L+"L ","") + if(PLM_HOTWTR_FUEL_TYPE_TXT<>"",PLM_HOTWTR_FUEL_TYPE_TXT+" ","electric ") + "water heater complete with PRV, thermostat and accessories as " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"approved manufacturer") + " or equal."
BILL No.6 — FIRE FIGHTING INSTALLATIONS
Bill 6 | Fire extinguishers | Specialty Equipment | [TYPE] portable fire extinguisher [CAPACITY]kg as [MFR] model [MODEL] or equal approved. | ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT, ASS_MODEL_NR_TXT |  | or equal approved. | NO | Count | BOQ-FLS-Extinguishers | CO2, powder, foam types
Bill 6 | Hose reels | Specialty Equipment | Swinging arm automatic semi-rigid hose reel [DIA]mm diameter and [LENGTH]m long to [STD] complete with all accessories as [MFR] or equal approved. | ASS_DESCRIPTION_TXT, RGL_STD_TXT, ASS_MANUFACTURER_TXT, ASS_MODEL_NR_TXT |  | or equal approved. | NO | Count | BOQ-FLS-HoseReels
Bill 6 | Sprinkler pipework | Pipes (sprinkler system) | [SZ]mm Black Seamless Steel SCH40 pipe complete with all accessories. | PLM_PPE_SZ_MM, PLM_PPE_MAT_TXT, PLM_PPE_PSR_RATING_BAR |  | complete with all accessories. | LM | Length | BOQ-FLS-Pipework | System type = sprinkler filter | if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + if(PLM_PPE_MAT_TXT<>"",PLM_PPE_MAT_TXT+" ","black steel ") + "sprinkler distribution pipe complete with fittings."
Bill 6 | Sprinkler heads | Sprinklers | Sprinkler heads [TEMP] deg C resistant. | FLS_SFTY_TEMP_RATING_C | Sprinkler heads | resistant. | NO | Count | BOQ-FLS-Sprinklers |  | if(FLS_SPK_TYPE_TXT<>"",FLS_SPK_TYPE_TXT,"Concealed pendant") + " sprinkler head " + if(FLS_SPK_ACTIVATION_TEMP_C<>"",FLS_SPK_ACTIVATION_TEMP_C+"°C ","68°C ") + if(FLS_SPK_COVERAGE_M2<>"",FLS_SPK_COVERAGE_M2+"m² coverage ","") + "complete with accessories."
BILL No.7 — HVAC INSTALLATIONS
Bill 7 | Indoor VRF units | Mechanical Equipment | [CAP]kW ([BTU] Btu/hr) Model: [MODEL] [TYPE] AC units. | HVC_CAP_KW, ASS_MODEL_NR_TXT, ASS_DESCRIPTION_TXT | Supply, installation, testing and commissioning of |  | NO | Count | BOQ-HVC-IndoorUnits | Group by type mark | if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"VRF") + " indoor " + if(HVC_UNIT_TYPE_TXT<>"",HVC_UNIT_TYPE_TXT,"cassette") + " unit " + if(HVC_CAP_KW<>"",HVC_CAP_KW+"kW cooling, ","TBC kW, ") + "complete with drain, remote control and accessories."
Bill 7 | Outdoor condensing units | Mechanical Equipment | Condensing unit of total cooling capacity [CAP]kW, [MODEL], Input: [PWR]kW ([PHS]Ph [VLT]V 50Hz). | HVC_CAP_KW, ASS_MODEL_NR_TXT, HVC_PWR_KW, ELC_PNL_PHS_COUNT_NR, HVC_VLT_V |  |  | NO | Count | BOQ-HVC-OutdoorUnits |  | if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"VRF") + " outdoor condensing unit " + if(HVC_CAP_KW<>"",HVC_CAP_KW+"kW cooling, ","TBC kW, ") + if(HVC_REFRIGERANT_TXT<>"",HVC_REFRIGERANT_TXT+" refrigerant, ","R410A, ") + if(HVC_EFF_RATIO_NR<>"",HVC_EFF_RATIO_NR+" COP, ","") + "complete with frame and vibration isolators."
Bill 7 | Refrigerant piping | Pipes (refrigerant system) | [SZ]mm refrigerant copper pipe. | PLM_PPE_SZ_MM |  |  | LM | Length | BOQ-HVC-RefrigPipework | System type filter | if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + "copper refrigerant " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"liquid/suction") + " pipe insulated, complete with fittings."
Bill 7 | Ductwork | Ducts | [CLASS]-class [MAT] duct [W]x[H]mm / DN[DIA]mm. | HVC_DUCT_CLASS_TXT, HVC_DCT_MAT_TXT, Width, Height |  |  | LM or SM | Length or Area | BOQ-HVC-Ducts | GI, flexible, insulated | "GMS " + if(HVC_DUCT_CLASS_TXT<>"",HVC_DUCT_CLASS_TXT,"Class B") + " duct " + if(HVC_DCT_SZ_W_MM<>"",HVC_DCT_SZ_W_MM+"W","?W") + "x" + if(HVC_DCT_SZ_H_MM<>"",HVC_DCT_SZ_H_MM+"H mm ","?H mm ") + "insulated complete with hangers." + if(HVC_VEL_MPS>8.0," [!VEL>8.0]","")
Bill 7 | Air terminals | Air Terminals | [TYPE] air terminal [SZ], [FLOW]m3/h. | HVC_DCT_TERMINAL_TYPE_SD_RG_EG_VAV_TXT, HVC_DCT_TERMINAL_SZ_TXT, HVC_DUCT_FLOWRATE_M3H |  |  | NO | Count | BOQ-HVC-AirTerminals | Diffusers, grilles, VAV | if(HVC_TERMINAL_TYPE_TXT<>"",HVC_TERMINAL_TYPE_TXT,"Supply grille") + " " + if(HVC_DCT_SZ_W_MM<>"",HVC_DCT_SZ_W_MM+"x","") + if(HVC_DCT_SZ_H_MM<>"",HVC_DCT_SZ_H_MM+"mm ","") + "complete with OBD and accessories." + if(HVC_DCT_TERMINAL_SOUND_DB_NR>35," [!NOISE>35dB]","")
BILL No.3 — ARCHITECTURE / STRUCTURE
Bill 3 | Walling | Walls | [THK]mm thick [TYPE] wall in [MORTAR] mortar. | BLE_WALL_THICKNESS_MM, BLE_WALL_CST_METHOD_TXT |  |  | SM | Area | BOQ-ARCH-Walling | Deduct openings separately | if(BLE_WALL_THICKNESS_MM<>"",BLE_WALL_THICKNESS_MM+"mm ","") + if(BLE_WALL_TYPE_CLASSIFICATION_TXT<>"",BLE_WALL_TYPE_CLASSIFICATION_TXT+" ","") + if(BLE_WALL_PRIMARY_WALL_MAT_TXT<>"",BLE_WALL_PRIMARY_WALL_MAT_TXT+" walling ","walling ") + if(BLE_WALL_FUNCTION_TXT<>"","("+BLE_WALL_FUNCTION_TXT+")","") + "." + if(PER_THERM_U_VALUE_W_M2K_NR>0.70," [!U>0.70 W/m²K]","")
Bill 3 | Floor finishes | Floors | [THK]mm [FINISH] floor finish. | BLE_FLR_FINISH_TXT, BLE_FLR_THICKNESS_MM |  |  | SM | Area | BOQ-ARCH-FloorFinishes | By finish type | if(BLE_FLR_MATERIAL_TXT<>"",BLE_FLR_MATERIAL_TXT+" ","") + if(BLE_FLR_TYPE_TXT<>"",BLE_FLR_TYPE_TXT+" ","") + "floor " + if(BLE_FLR_TILE_SZ_MM<>"",BLE_FLR_TILE_SZ_MM+"mm tile ","tiles") + "laid to falls where required."
Bill 3 | Doors | Doors | [W]x[H]mm [OP] door in [MAT] with [HW] hardware. | BLE_DOOR_WIDTH_MM, BLE_DOOR_HEIGHT_MM, BLE_DOOR_OPERATION_TYPE, BLE_DOOR_MATERIAL_FINISH_TXT, BLE_DOOR_HARDWARE_SPECIFICATION_TXT |  |  | NO | Count | BOQ-ARCH-Doors | Include ironmongery set
Bill 3 | Windows | Windows | [W]x[H]mm [OP] [GLAZING] window. | BLE_WINDOW_WIDTH_MM, BLE_WINDOW_HEIGHT_MM, BLE_WINDOW_OPERATION_TYPE_TXT, BLE_WINDOW_GLAZING_TYPE_TXT |  |  | NO | Count | BOQ-ARCH-Windows | Include glass spec | if(BLE_WINDOW_OPERATION_TYPE_TXT<>"",BLE_WINDOW_OPERATION_TYPE_TXT+" ","") + "window " + if(BLE_WINDOW_WIDTH_MM<>"",BLE_WINDOW_WIDTH_MM+"W","?W") + "x" + if(BLE_WINDOW_HEIGHT_MM<>"",BLE_WINDOW_HEIGHT_MM+"H mm","?H mm") + ", " + if(BLE_WINDOW_GLAZING_TYPE_TXT<>"",BLE_WINDOW_GLAZING_TYPE_TXT+" glazed,","glazed,") + " frame: " + if(BLE_WINDOW_FRAME_MAT_TXT<>"",BLE_WINDOW_FRAME_MAT_TXT+",","TBC,") + " including ironmongery, mosquito screen, burglar bar." + if(BLE_WINDOW_U_VALUE_W_M_2K_NR>3.0," [!U>3.0]","") + if(BLE_WINDOW_SOLAR_HEAT_GAIN_COEFFICIENT_NR>0.40," [!SHGC>0.40]","")
Bill 3 | Roofing | Roofs | [TYPE] roofing complete with all accessories. | ASS_DESCRIPTION_TXT |  | complete with all accessories. | SM | Area | BOQ-ARCH-Roofing | Gauge, profile from type | if(BLE_ROOF_TYPE_TXT<>"",BLE_ROOF_TYPE_TXT+" ","") + if(BLE_ROOF_MATERIAL_TXT<>"",BLE_ROOF_MATERIAL_TXT+" roofing ","roofing ") + "to " + if(BLE_ROOF_PITCH_DEG<>"",BLE_ROOF_PITCH_DEG+"° pitch.","as drawings.") + if(PER_THERM_U_VALUE_W_M2K_NR>0.50," [!U>0.50 W/m²K roof]","")
Bill 3 | Ceiling finishes | Ceilings | [TYPE] ceiling. | ASS_DESCRIPTION_TXT |  |  | SM | Area | BOQ-ARCH-Ceilings | Suspended, plastered, etc.
Bill 3 | Stairs | Stairs | [MAT] staircase [W]mm wide, [RISE]mm rise, [GOING]mm going, with [FINISH] tread finish and [HR_MAT] handrail. | BLE_STAIR_MAT, BLE_STAIR_WIDTH_MM, BLE_STAIR_RISE_MM, BLE_STAIR_GOING_MM, BLE_STAIR_TREAD_FINISH, BLE_STAIR_HANDRAIL_MAT |  |  | NR/FLIGHT | Count | BOQ-ARCH-Stairs
Bill 3 | RC columns | Structural Columns | [SZ] reinforced concrete column, [GRADE] grade. | BLE_STRUCT_COLUMN_SZ_TXT, BLE_STRUCT_CONCRETE_GRADE_TXT |  |  | NR | Count | BOQ-STR-Columns | Links to rebar schedule | "Grade " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"C30") + " RC column " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"as drawings") + " reinforced per BBS."
Bill 3 | RC beams | Structural Framing | [SZ] reinforced concrete beam, [GRADE] grade. | BLE_STRUCT_BEAM_SZ_TXT, BLE_STRUCT_CONCRETE_GRADE_TXT |  |  | LM | Length | BOQ-STR-Framing |  | "Grade " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"C30") + " RC beam " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"as drawings") + " reinforced per BBS."
Bill 3 | Foundations | Structural Foundations | [SZ] foundation in [GRADE] concrete with [REINF] reinforcement. | BLE_STRUCT_FOUNDATION_SZ_TXT, BLE_STRUCT_CONCRETE_GRADE_TXT, BLE_STRUCT_REINFORCEMENT |  |  | CM | Volume | BOQ-STR-Foundations | Pad, strip, raft
BILL No.9 — ICT INSTALLATIONS
Bill 9 | Data outlets | Data Devices | Cat[CAT] [TYPE] data outlet point in [CDT_SZ]mm PVC conduit complete with all accessories. | ICT_OUTLET_TYPE_TXT, ELC_CDT_SZ_MM |  | complete with all accessories. | NO | Count | BOQ-ICT-DataOutlets | Cat5e/Cat6/Cat6A | "Cat " + if(ICT_CAT_RATING_TXT<>"",ICT_CAT_RATING_TXT,"6") + " data outlet in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"concealed") + " conduit, " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"Panduit or equal") + " complete with faceplate and accessories."
Bill 9 | CCTV cameras | Security Devices | [TYPE] CCTV camera point in [CDT_SZ]mm PVC conduit complete with all accessories. | ASS_DESCRIPTION_TXT, ELC_CDT_SZ_MM |  | complete with all accessories. | NO | Count | BOQ-ELC-Security |  | "CCTV " + if(SEC_DEV_TYPE_TXT<>"",SEC_DEV_TYPE_TXT,"dome camera") + " in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " PVC concealed conduit, " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"Hikvision or equal") + " complete with bracket and accessories."
Bill 9 | BMS controllers | Communication Devices | [TYPE] BMS controller, [PROTOCOL], BACnet instance [ID]. | COM_C_DEV_TYPE_TXT, COM_C_NETWORK_ADDRESS_TXT, COM_C_DEV_BACNET_INSTANCE_INT |  |  | NO | Count | BOQ-ICT-BMS |  | if(COM_C_DEV_TYPE_TXT<>"",COM_C_DEV_TYPE_TXT,"BMS controller") + " BACnet/IP, instance " + if(COM_C_DEV_BACNET_INSTANCE_INT<>"",COM_C_DEV_BACNET_INSTANCE_INT,"?") + " complete with I/O, power supply and housing."
Bill 3 | Ceilings | Ceilings | [MATERIAL] [TYPE] ceiling system [MODULE]mm at [HEIGHT]mm FFL | BLE_CEIL_MATERIAL_TXT, BLE_CEIL_TYPE_TXT, BLE_CEIL_MODULE_MM, BLE_CEIL_HEIGHT_MM |  | complete with all accessories. | m² | Area | BOQ-ARCH-Ceilings | Group by type mark. Acoustic warning if noise > 40dB.
Bill 3 | Roofing | Roofs | [TYPE] [MATERIAL] roofing [GAUGE] to [PITCH]° pitch with all accessories | BLE_ROOF_TYPE_TXT, BLE_ROOF_MATERIAL_TXT, BLE_ROOF_PITCH_DEG |  | complete with all accessories. | m² | Area | BOQ-ARCH-Roofing | U-value warning for roof > 0.50 W/m²K. | if(BLE_ROOF_TYPE_TXT<>"",BLE_ROOF_TYPE_TXT+" ","") + if(BLE_ROOF_MATERIAL_TXT<>"",BLE_ROOF_MATERIAL_TXT+" roofing ","roofing ") + "to " + if(BLE_ROOF_PITCH_DEG<>"",BLE_ROOF_PITCH_DEG+"° pitch.","as drawings.") + if(PER_THERM_U_VALUE_W_M2K_NR>0.50," [!U>0.50 W/m²K roof]","")
Bill 3 | RC Columns | Structural Columns | Grade [GRADE] RC columns [DESC], reinforced per BBS | BLE_STRUCT_CONCRETE_GRADE_TXT, ASS_DESCRIPTION_TXT | Grade | reinforced per BBS. | m³ | Volume | BOQ-STR-Columns | Group by column mark.
Bill 3 | Foundations | Structural Foundations | Grade [GRADE] concrete foundations [THICKNESS]mm thick, reinforced per BBS | BLE_STRUCT_CONCRETE_GRADE_TXT, BLE_STRUCT_THICKNESS_MM | Grade | reinforced per BBS. | m³ | Volume | BOQ-STR-Foundations | Pad, strip, raft — group by type.
Bill 3 | Stairs | Stairs | [MATERIAL] stair [RISE]R/[GOING]G mm, [WIDTH]mm wide, [TREAD] tread, [HANDRAIL] handrail | BLE_STAIR_MAT_TXT, BLE_STAIR_RISE_MM, BLE_STAIR_GOING_MM, BLE_STAIR_WIDTH_MM, BLE_STAIR_TREAD_FINISH_TXT |  | complete with handrail and balustrade. | Flight | Count | BOQ-ARCH-Stairs | Warning: rise > 190 or width < 1000mm.
Bill 3 | Access ramps | Ramps | Access ramp [SLOPE]% gradient, [SURFACE] surface, handrails both sides, [WIDTH]mm clear | BLE_RAMP_SLOPE_PCT, BLE_RAMP_SURFACE_FINISH_TXT, RGL_ACCESS_CLEAR_WIDTH_MM | Ramp at | complete with handrails and nosings. | LM | Length | BOQ-ARCH-Ramps | Warning: slope > 8.33%, width < 900mm. Uganda PWD Act.
Bill 7 | Flex ducts | Flex Ducts | [DIA]mm flexible duct [LENGTH]mm long connecting rigid duct to terminal | HVC_DCT_FLEX_DIA_MM, HVC_DCT_FLEX_MAX_LEN_MM |  | complete with clamps, max 1500mm per SMACNA. | No. | Count | BOQ-HVC-FlexDucts | Warning: length > 1500mm.
Bill 7 | Duct accessories | Duct Accessories | [TYPE] duct accessory [SIZE]mm including all fixings | HVC_DCT_ACC_TYPE_TXT, HVC_DCT_SZ_W_MM |  | complete with fixings and accessories. | No. | Count | BOQ-HVC-DuctAcc | Dampers, attenuators, fire dampers — group by type.
Bill 8 | Passenger lifts | Specialty Equipment | [BRAND] [CAPACITY]kg [STOPS]-stop passenger lift [SPEED]m/s complete with all accessories | ASS_MANUFACTURER_TXT, ASS_CAPACITY_TXT, ASS_DESCRIPTION_TXT |  | complete with landing doors, controls, emergency phone. | No. | Count | BOQ-LIFT-Equipment | Uganda: BS EN 81-20. Govt lift inspector cert.
Bill 9 | Generator | Specialty Equipment | [BRAND] [CAPACITY]kVA diesel generator with canopy, ATS, complete with commissioning | ASS_MANUFACTURER_TXT, ASS_CAPACITY_TXT, ASS_DESCRIPTION_TXT |  | complete with base tank, ATS panel, wiring. | No. | Count | BOQ-ELEC-Generator | Uganda: essential for commercial/institutional buildings.
Bill 9 | Nurse call points | Nurse Call Devices | [TYPE] nurse call point zone [ZONE] complete with pull cord, indicator, and accessories | NCL_CALL_TYPE_TXT, NCL_ZONE_TXT |  | connected to master panel. | No. | Count | BOQ-ICT-NurseCall | HTM 08-03. Healthcare projects only.
Bill 3 | Internal plaster / paint | Walls | [FINISH] two coats on all internal plastered wall faces | BLE_WALL_INTERIOR_FINISH_TXT |  | to all internal faces. | m² | Area | BOQ-ARCH-InternalPlaster | Colour from room data sheet. Paint type from spec. | if(BLE_WALL_INTERIOR_FINISH_TXT<>"",BLE_WALL_INTERIOR_FINISH_TXT,"[COLOUR]") + " paint two coats on internal plastered walls."
Bill 7 | HVAC equipment (combined) | Mechanical Equipment | [TYPE] HVAC unit [CAPACITY]kW complete with all accessories | HVC_CAP_KW, ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT |  | complete with all accessories. | No. | Count | BOQ-HVC-Equipment | Covers VRF indoor+outdoor, splits, AHUs when grouped. | if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"HVAC") + " " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"") + " " + if(HVC_CAP_KW<>"",HVC_CAP_KW+"kW ","") + "complete with all accessories."

## 05-NEW-PARAMETERS-v4.2
NEW PARAMETERS FOR v4.2 ¦ Paragraph containers for gap categories + warning threshold params + BOQ schedule params
Parameter name | Type | Group | Discipline | Binding | Category scope | Description | Source | Priority
v4.2 PARAGRAPH ENGINE — 3-state visibility (3 params)
TAG_PARA_STATE_1_BOOL | YESNO | TAG_STYLE | MULTI | Type | All 53 | Compact mode (tier 1 only) | v4.2 new | IMMEDIATE
TAG_PARA_STATE_2_BOOL | YESNO | TAG_STYLE | MULTI | Type | All 53 | Standard mode (tiers 1+2) | v4.2 new | IMMEDIATE
TAG_PARA_STATE_3_BOOL | YESNO | TAG_STYLE | MULTI | Type | All 53 | Comprehensive mode (tiers 1+2+3) | v4.2 new | IMMEDIATE
v4.2 GAP CATEGORY PARAGRAPH CONTAINERS (18 params)
PLM_TAG_7_PARA_FIXTURE_TXT | TEXT | PLM_TAG | PLUMBING | Type | Plumbing Fixtures | Sanitary fixture paragraph | v4.2 new | IMMEDIATE
PLM_TAG_7_PARA_EQUIPMENT_TXT | TEXT | PLM_TAG | PLUMBING | Type | Plumbing Equipment | Plumbing equipment paragraph | v4.2 new | IMMEDIATE
PLM_TAG_7_PARA_PIPEACC_TXT | TEXT | PLM_TAG | PLUMBING | Type | Pipe Accessories | Pipe accessory paragraph | v4.2 new | HIGH
ELC_TAG_7_PARA_CONDUIT_TXT | TEXT | ELC_TAG | ELECTRICAL | Type | Conduits, Conduit Fittings | Conduit paragraph | v4.2 new | HIGH
ELC_TAG_7_PARA_TRAY_TXT | TEXT | ELC_TAG | ELECTRICAL | Type | Cable Trays, Cable Tray Fittings | Cable tray paragraph | v4.2 new | HIGH
HVC_TAG_7_PARA_FLEXDUCT_TXT | TEXT | HVC_TAG | HVAC | Type | Flex Ducts | Flex duct paragraph | v4.2 new | HIGH
HVC_TAG_7_PARA_DCTACC_TXT | TEXT | HVC_TAG | HVAC | Type | Duct Accessories | Duct accessory paragraph | v4.2 new | HIGH
ARCH_TAG_7_PARA_FACADE_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Curtain Panels, CW Mullions | Facade/curtain wall paragraph | v4.2 new | HIGH
ARCH_TAG_7_PARA_STAIR_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Stairs | Stair paragraph | v4.2 new | HIGH
ARCH_TAG_7_PARA_RAMP_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Ramps | Ramp paragraph | v4.2 new | HIGH
STR_TAG_7_PARA_FDN_TXT | TEXT | STR_TAG | ARCHITECTURAL | Type | Structural Foundations | Foundation paragraph | v4.2 new | HIGH
ARCH_TAG_7_PARA_CASEWORK_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Casework | Casework paragraph | v4.2 new | MEDIUM
ARCH_TAG_7_PARA_FURNITURE_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Furniture | Furniture paragraph | v4.2 new | MEDIUM
ASS_TAG_7_PARA_EQUIPMENT_TXT | TEXT | ASS_TAG | MULTI | Type | Specialty Equipment | Specialty equipment paragraph | v4.2 new | MEDIUM
COM_TAG_7_PARA_BMS_TXT | TEXT | COM_TAG | ELECTRICAL | Type | Communication Devices | BMS device paragraph | v4.2 new | HIGH
ICT_TAG_7_PARA_DATA_TXT | TEXT | ICT_TAG | ELECTRICAL | Type | Data Devices, Telephone Devices | Data/telephone outlet paragraph | v4.2 new | MEDIUM
NCL_TAG_7_PARA_NURSECALL_TXT | TEXT | NCL_TAG | ELECTRICAL | Type | Nurse Call Devices | Nurse call paragraph | v4.2 new | PROJECT
SEC_TAG_7_PARA_SECURITY_TXT | TEXT | SEC_TAG | ELECTRICAL | Type | Security Devices | Security device paragraph | v4.2 new | MEDIUM
v4.2 TIER-3 UNIVERSAL PARAGRAPH CONTAINERS — docx s6.2 (5 params)
RGL_TAG_7_PARA_COMPLIANCE_TXT | TEXT | RGL_TAG | MULTI | Type | All 53 (tier 3) | Regulatory compliance paragraph (KCCA, UMEME, NWSC, NEMA approvals, QA) | v4.2 new | HIGH
PER_TAG_7_PARA_ENVIRONMENT_TXT | TEXT | PER_TAG | MULTI | Type | All 53 (tier 3) | Environmental context paragraph (climate zone, humidity, altitude, rainfall, termite protection) | v4.2 new | HIGH
CST_TAG_7_PARA_CONCRETE_TXT | TEXT | CST_TAG | STR/ARCH | Type | Generic (structural) | Concrete/masonry specification paragraph (grade, strength, admixture, mix ratio) | v4.2 new | HIGH
PLM_TAG_7_PARA_DRAIN_TXT | TEXT | PLM_TAG | PLUMBING | Type | Pipes (drainage only) | Drainage paragraph (trap type, cleanout, vent terminals, expansion joints, strainers) | v4.2 new | HIGH
ELC_TAG_7_PARA_CABLE_TXT | TEXT | ELC_TAG | ELECTRICAL | Type | Cable Trays, Conduits | Cable paragraph (destination, source, cores, size, insulation, install method, tray fill, load) | v4.2 new | HIGH
v4.2 WARNING THRESHOLD REFERENCE PARAMS (3 new system params)
TAG_WARN_VISIBLE_BOOL | YESNO | TAG_STYLE | MULTI | Type | All 53 | Enable/disable warning text in tags | v4.2 new | IMMEDIATE
TAG_WARN_SEVERITY_FILTER_TXT | TEXT | TAG_STYLE | MULTI | Type | Project Information | Filter: CRITICAL, HIGH, MEDIUM, ALL | v4.2 new | HIGH
ELC_PNL_RATED_KW | NUMBER | ELC_PWR | ELECTRICAL | Type | Electrical Equipment | Panel rated capacity kW (for overload check) | v4.2 new | HIGH
TOTAL: 3 visibility + 18 paragraph containers + 5 tier-3 universal + 3 warning system = 29 new parameters
v4.3 RE-REGISTERED v4.1 CONTAINERS + NEW v4.3 CONTAINERS (18 params)
ARCH_TAG_7_PARA_WALL_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Walls | Wall paragraph container | v4.1 + v4.3 unified | IMMEDIATE
ARCH_TAG_7_PARA_FLOOR_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Floors | Floor paragraph container | v4.1 + v4.3 unified | IMMEDIATE
ARCH_TAG_7_PARA_DOOR_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Doors | Door paragraph container | v4.1 + v4.3 unified | IMMEDIATE
ARCH_TAG_7_PARA_WIN_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Windows | Window paragraph container | v4.1 + v4.3 unified | IMMEDIATE
ARCH_TAG_7_PARA_ROOM_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Rooms | Room/space paragraph container | v4.1 + v4.3 unified | IMMEDIATE
ARCH_TAG_7_PARA_CEIL_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Ceilings | Ceiling paragraph container — NEW v4.3 | v4.3 new | HIGH
ARCH_TAG_7_PARA_ROOF_TXT | TEXT | ARCH_TAG | ARCHITECTURAL | Type | Roofs | Roof paragraph container — NEW v4.3 | v4.3 new | HIGH
STR_TAG_7_PARA_COL_TXT | TEXT | STR_TAG | STRUCTURAL | Type | Structural Columns | Column paragraph container | v4.1 + v4.3 unified | HIGH
STR_TAG_7_PARA_BEAM_TXT | TEXT | STR_TAG | STRUCTURAL | Type | Structural Framing | Beam/framing paragraph container | v4.1 + v4.3 unified | HIGH
HVC_TAG_7_PARA_SPEC_TXT | TEXT | HVC_TAG | HVAC | Type | Mechanical Equipment | HVAC equipment paragraph container | v4.1 + v4.3 unified | IMMEDIATE
HVC_TAG_7_PARA_DUCT_TXT | TEXT | HVC_TAG | HVAC | Type | Ducts, Duct Fittings | Duct paragraph container | v4.1 + v4.3 unified | IMMEDIATE
HVC_TAG_7_PARA_AT_TXT | TEXT | HVC_TAG | HVAC | Type | Air Terminals | Air terminal paragraph container | v4.1 + v4.3 unified | IMMEDIATE
ELC_TAG_7_PARA_PANEL_TXT | TEXT | ELC_TAG | ELECTRICAL | Type | Electrical Equipment | DB panel paragraph container | v4.1 + v4.3 unified | IMMEDIATE
LTG_TAG_7_PARA_SPEC_TXT | TEXT | LTG_TAG | ELECTRICAL | Type | Lighting Fixtures | Lighting fixture paragraph container | v4.1 + v4.3 unified | IMMEDIATE
ELC_TAG_7_PARA_CIRCUIT_TXT | TEXT | ELC_TAG | ELECTRICAL | Type | Electrical Fixtures | Circuit/point paragraph container | v4.1 + v4.3 unified | IMMEDIATE
PLM_TAG_7_PARA_PIPE_TXT | TEXT | PLM_TAG | PLUMBING | Type | Pipes, Pipe Fittings | Pipe paragraph container — NEW v4.3 | v4.3 new | HIGH
FLS_TAG_7_PARA_FA_TXT | TEXT | FLS_TAG | FIRE | Type | Fire Alarm Devices | Fire alarm paragraph container — NEW v4.3 | v4.3 new | HIGH
FLS_TAG_7_PARA_SPR_TXT | TEXT | FLS_TAG | FIRE | Type | Sprinklers | Sprinkler paragraph container — NEW v4.3 | v4.3 new | HIGH

## 06-VALIDATION-CHECKLIST
VALIDATION CHECKLIST v4.2
Check | Validation | Severity | Automated? | Sheet ref | Notes
V-01 | All v4.2 paragraph params exist in MR_PARAMETERS.csv | CRITICAL | Yes | 05 | 18 new containers
V-02 | All v4.2 paragraph formula source params exist in MR_PARAMETERS | CRITICAL | Yes | 03 | Cross-ref calculated value formulas
V-03 | All v4.2 paragraph params have Data_Type = TEXT | HIGH | Yes | 05
V-04 | 3-state visibility booleans registered in MR_PARAMETERS | CRITICAL | Yes | 05 | TAG_PARA_STATE_1/2/3_BOOL
V-05 | Warning threshold params exist for all CRITICAL/HIGH severity checks | HIGH | Yes | 02 | 34 threshold checks
V-06 | Warning formula patterns valid in Revit calculated value syntax | HIGH | Manual | 02 | Test in Revit 2025/2026/2027
V-07 | All 47 categories have at least one Tag 7 paragraph or shared reference | HIGH | Yes | 01 | 47/47 target
V-08 | BOQ schedule calculated values produce valid natural-language descriptions | HIGH | Manual | 04 | Test with sample model export
V-09 | No duplicate GUID in MR_PARAMETERS after adding 24 new params | CRITICAL | Yes | 05 | VALIDAT_BIM_TEMPLATE check G-01
V-10 | CATEGORY_BINDINGS updated for all 18 new paragraph container params | CRITICAL | Yes | 01 | Each container bound to its category scope
V-11 | Warning severity filter respects TAG_WARN_SEVERITY_FILTER_TXT setting | MEDIUM | Manual | 02 | CRITICAL/HIGH/MEDIUM/ALL
V-12 | Backward compatibility: v4.1 projects load without errors | CRITICAL | Manual | — | STING Tools parameter sync adds defaults
V-13 | Tag performance benchmark: 1000 elements with warnings < 3 sec regen | HIGH | Manual | — | Profile in Revit journal
V-14 | All BOQ schedules export cleanly to Excel with no formula errors | HIGH | Manual | 04 | Export + spot check
V-15 | Sheet 07 unified paragraph engine replaces 3-paragraph plan in all 47 categories | HIGH | Yes | 07 | v4.3 unified engine check
V-16 | All 36 Tag 7 param names in Sheet 07 registered in Sheet 05 | CRITICAL | Yes | 05 | 36 params incl 18 re-registered v4.1
V-17 | Sheet 04 and Sheet 08 schedule names fully aligned (no BOQ-HVAC- vs BOQ-HVC- mismatches) | HIGH | Yes | 04,08 | Standardised to BOQ-HVC- prefix
V-18 | Sheet 04 Col L (BOQ_DESC_FORMULA) provides paste-ready Revit formulas for all 28 automated elements | HIGH | Manual | 04 | Copy from Col L → Revit Edit Label
V-19 | All Sheet 08 item rows with Revit category have matching schedule in Sheet 04 | HIGH | Yes | 04,08 | Cross-ref by schedule name
V-20 | Warning param formulas updated for ICT/Security/Specialty/NurseCall categories | MEDIUM | Manual | 07 | Previously had NO WARNING entries

## 07-PARA-ENGINE-UNIFIED
TAG 7 PARAGRAPH ENGINE — UNIFIED REFERENCE v4.3 ¦ Supersedes 3-paragraph plan ¦ All categories ¦ Source: advisory_v1_0.docx + v4.2 tag guide
ARCHITECTURE: Tag 7 is the single paragraph container tier. The old "3-paragraph plan" (separate para per category type) is SUPERSEDED. v4.3 uses one unified paragraph tag per category class, with 3 additive DEPTH STATES gated by YES/NO params: TAG_PARA_STATE_1_BOOL=compact (State 1 only) ¦ TAG_PARA_STATE_2_BOOL=standard (States 1+2) ¦ TAG_PARA_STATE_3_BOOL=comprehensive (States 1+2+3) Each state adds a calculated-value label. Empty params collapse via if(PARAM<>"", PARAM, ""). Warning flags auto-append via if(PARAM > MAX, " [!WARNING]", "").
Category | Disc. | Tag 7 Param Name | Tag Family | STATE 1 — Compact formula (all states show this) | STATE 2 — Standard formula (states 2+3 show this) | STATE 3 — Comprehensive formula (state 3 only) | S1 param pool | S2 param pool | S3 param pool | Warning params + formula | BOQ map ref | Revit schedule name | Priority
TIER 1/2 — UNIVERSAL CATEGORIES ¦ Covered v4.1, paragraph engine adds S2 and S3 depth
Walls | ARCH | ARCH_TAG_7_PARA_WALL_TXT | ARCH_Wall_Para.rfa | if(BLE_WALL_FUNCTION_TXT<>"",BLE_WALL_FUNCTION_TXT,"This") + " wall is " + if(BLE_WALL_THICKNESS_MM<>"",BLE_WALL_THICKNESS_MM+"mm thick","of unspecified thickness") + ", constructed by " + if(BLE_WALL_CST_METHOD_TXT<>"",BLE_WALL_CST_METHOD_TXT,"unspecified method") + ". Primary material: " + if(BLE_WALL_PRIMARY_WALL_MAT_TXT<>"",BLE_WALL_PRIMARY_WALL_MAT_TXT,"TBC") + ". Type: " + if(BLE_WALL_TYPE_CLASSIFICATION_TXT<>"",BLE_WALL_TYPE_CLASSIFICATION_TXT,"unclassified") + "." | "Thermal: U=" + if(PER_THERM_U_VALUE_W_M2K_NR<>"",PER_THERM_U_VALUE_W_M2K_NR+"W/m²K","TBC") + ", R=" + if(PER_THERM_R_VALUE_M2K_W<>"",PER_THERM_R_VALUE_M2K_W+"m²K/W","TBC") + ". Condensation: " + if(PER_THERM_CONDENSATION_RISK_TXT<>"",PER_THERM_CONDENSATION_RISK_TXT,"not assessed") + ". STC: " + if(BLE_WALL_SOUND_TRANSMISSION_CLASS_RATING_NR<>"",BLE_WALL_SOUND_TRANSMISSION_CLASS_RATING_NR,"TBC") + ". FRR: " + if(FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN<>"",FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN+"min","N/A") + "." | "Recycled: " + if(PER_SUST_RECYCLED_CONTENT_PCT<>"",PER_SUST_RECYCLED_CONTENT_PCT+"%","N/A") + ". Carbon: " + if(PER_SUST_CARBON_FOOTPRINT_KG<>"",PER_SUST_CARBON_FOOTPRINT_KG+"kgCO2e","N/A") + ". Density: " + if(PROP_DENSITY_KG_M3<>"",PROP_DENSITY_KG_M3+"kg/m³","N/A") + ". Finish int: " + if(BLE_WALL_INTERIOR_FINISH_TXT<>"",BLE_WALL_INTERIOR_FINISH_TXT,"TBC") + ", ext: " + if(BLE_WALL_EXTERIOR_FINISH_TXT<>"",BLE_WALL_EXTERIOR_FINISH_TXT,"TBC") + ". Moisture barrier: " + if(BLE_WALL_MOISTURE_BARRIER_INCLUDED_TXT<>"",BLE_WALL_MOISTURE_BARRIER_INCLUDED_TXT,"TBC") + ". Standard: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"N/A") + "." | BLE_WALL_FUNCTION_TXT, BLE_WALL_THICKNESS_MM, BLE_WALL_CST_METHOD_TXT, BLE_WALL_PRIMARY_WALL_MAT_TXT, BLE_WALL_TYPE_CLASSIFICATION_TXT | PER_THERM_U_VALUE_W_M2K_NR, PER_THERM_R_VALUE_M2K_W, PER_THERM_CONDENSATION_RISK_TXT, BLE_WALL_SOUND_TRANSMISSION_CLASS_RATING_NR, FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN | PER_SUST_RECYCLED_CONTENT_PCT, PER_SUST_CARBON_FOOTPRINT_KG, PROP_DENSITY_KG_M3, BLE_WALL_INTERIOR_FINISH_TXT, BLE_WALL_EXTERIOR_FINISH_TXT, BLE_WALL_MOISTURE_BARRIER_INCLUDED_TXT, RGL_STD_TXT | PER_THERM_U_VALUE_W_M2K_NR > 0.70 → [!U > 0.70] FLS_PROT...< 30 → [!FRR < 30] | BOQ-ARCH-Walling (sh.08) Bill No.3: [THK]mm [TYPE] wall | BOQ-ARCH-Walling | IMMEDIATE
Floors | ARCH | ARCH_TAG_7_PARA_FLOOR_TXT | ARCH_Floor_Para.rfa | if(BLE_FLR_TYPE_TXT<>"",BLE_FLR_TYPE_TXT,"Floor") + ": " + if(BLE_FLR_FINISH_TXT<>"",BLE_FLR_FINISH_TXT,"finish TBC") + ", " + if(BLE_FLR_THICKNESS_MM<>"",BLE_FLR_THICKNESS_MM+"mm thick","thickness TBC") + ". Subfloor: " + if(BLE_FLR_SUBFLOOR_TXT<>"",BLE_FLR_SUBFLOOR_TXT,"TBC") + "." | "Thermal: U=" + if(PER_THERM_U_VALUE_W_M2K_NR<>"",PER_THERM_U_VALUE_W_M2K_NR+"W/m²K","TBC") + ". DPM: " + if(BLE_FLR_MOISTURE_BARRIER_TXT<>"",BLE_FLR_MOISTURE_BARRIER_TXT,"TBC") + ". Structural rating: " + if(BLE_FLR_STRUCTURAL_RATING_TXT<>"",BLE_FLR_STRUCTURAL_RATING_TXT,"TBC") + "." | "Procurement: " + if(CST_S_SUPPLIER_TXT<>"",CST_S_SUPPLIER_TXT,"TBC") + ". Unit rate: " + if(CST_S_UNIT_RATE_UGX_NR<>"",CST_S_UNIT_RATE_UGX_NR+" UGX/m²","TBC") + ". EPD: " + if(MAT_EPD_REF_TXT<>"",MAT_EPD_REF_TXT,"N/A") + ". RGL: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"N/A") + "." | BLE_FLR_TYPE_TXT, BLE_FLR_FINISH_TXT, BLE_FLR_THICKNESS_MM, BLE_FLR_SUBFLOOR_TXT | PER_THERM_U_VALUE_W_M2K_NR, BLE_FLR_MOISTURE_BARRIER_TXT, BLE_FLR_STRUCTURAL_RATING_TXT | CST_S_SUPPLIER_TXT, CST_S_UNIT_RATE_UGX_NR, MAT_EPD_REF_TXT, RGL_STD_TXT | PER_THERM_U_VALUE_W_M2K_NR > 0.70 → [!U > 0.70] | BOQ-ARCH-FloorFinish (sh.08) Bill No.3: [THK]mm [FINISH] floor | BOQ-ARCH-FloorFinish | IMMEDIATE
Ceilings | ARCH | ARCH_TAG_7_PARA_CEIL_TXT | ARCH_Ceil_Para.rfa | if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"Ceiling type TBC") + ". Suspension: " + if(BLE_CEIL_SUSPENSION_TXT<>"",BLE_CEIL_SUSPENSION_TXT,"TBC") + ". Grid: " + if(BLE_CEIL_GRID_MM<>"",BLE_CEIL_GRID_MM+"mm","TBC") + "." | "Acoustic: NRC=" + if(PER_ACOUSTICS_NRC_NR<>"",PER_ACOUSTICS_NRC_NR,"TBC") + ", background noise=" + if(PER_ACOUSTICS_BACKGROUND_NOISE_DB<>"",PER_ACOUSTICS_BACKGROUND_NOISE_DB+"dB","TBC") + ". Thermal: U=" + if(PER_THERM_U_VALUE_W_M2K_NR<>"",PER_THERM_U_VALUE_W_M2K_NR+"W/m²K","TBC") + "." | "Supplier: " + if(CST_S_SUPPLIER_TXT<>"",CST_S_SUPPLIER_TXT,"TBC") + ". FRR: " + if(FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN<>"",FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN+"min","N/A") + ". EPD: " + if(MAT_EPD_REF_TXT<>"",MAT_EPD_REF_TXT,"N/A") + "." | ASS_DESCRIPTION_TXT, BLE_CEIL_SUSPENSION_TXT, BLE_CEIL_GRID_MM | PER_ACOUSTICS_NRC_NR, PER_ACOUSTICS_BACKGROUND_NOISE_DB, PER_THERM_U_VALUE_W_M2K_NR | CST_S_SUPPLIER_TXT, FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN, MAT_EPD_REF_TXT | PER_ACOUSTICS_BACKGROUND_NOISE_DB > 40 → [!NOISE > 40dB] [NEW v4.3 container] | BOQ-ARCH-Ceilings (sh.08) Bill No.3: [TYPE] ceiling | BOQ-ARCH-Ceilings | HIGH
Roofs | ARCH | ARCH_TAG_7_PARA_ROOF_TXT | ARCH_Roof_Para.rfa | if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"Roof type TBC") + ". Pitch: " + if(BLE_ROOF_PITCH_DEG<>"",BLE_ROOF_PITCH_DEG+"°","TBC") + ". Primary material: " + if(BLE_ROOF_PRIMARY_MAT_TXT<>"",BLE_ROOF_PRIMARY_MAT_TXT,"TBC") + "." | "Thermal: U=" + if(PER_THERM_U_VALUE_W_M2K_NR<>"",PER_THERM_U_VALUE_W_M2K_NR+"W/m²K","TBC") + ". Insulation: " + if(BLE_ROOF_INSULATION_TXT<>"",BLE_ROOF_INSULATION_TXT,"TBC") + ". Waterproofing: " + if(BLE_ROOF_WATERPROOFING_TXT<>"",BLE_ROOF_WATERPROOFING_TXT,"TBC") + "." | "Carbon: " + if(PER_SUST_CARBON_FOOTPRINT_KG<>"",PER_SUST_CARBON_FOOTPRINT_KG+"kgCO2e","N/A") + ". Standard: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"N/A") + ". Supplier: " + if(CST_S_SUPPLIER_TXT<>"",CST_S_SUPPLIER_TXT,"TBC") + "." | ASS_DESCRIPTION_TXT, BLE_ROOF_PITCH_DEG, BLE_ROOF_PRIMARY_MAT_TXT | PER_THERM_U_VALUE_W_M2K_NR, BLE_ROOF_INSULATION_TXT, BLE_ROOF_WATERPROOFING_TXT | PER_SUST_CARBON_FOOTPRINT_KG, RGL_STD_TXT, CST_S_SUPPLIER_TXT | PER_THERM_U_VALUE_W_M2K_NR > 0.50 → [!U > 0.50] [NEW v4.3 container] | BOQ-ARCH-Roofing (sh.08) Bill No.3: [TYPE] roofing | BOQ-ARCH-Roofing | HIGH
Doors | ARCH | ARCH_TAG_7_PARA_DOOR_TXT | ARCH_Door_Para.rfa | if(BLE_DOOR_WIDTH_MM<>"",BLE_DOOR_WIDTH_MM,"?") + "x" + if(BLE_DOOR_HEIGHT_MM<>"",BLE_DOOR_HEIGHT_MM,"?") + "mm " + if(BLE_DOOR_OPERATION_TYPE_TXT<>"",BLE_DOOR_OPERATION_TYPE_TXT,"") + " door, " + if(BLE_DOOR_MATERIAL_FINISH_TXT<>"",BLE_DOOR_MATERIAL_FINISH_TXT,"material TBC") + " frame and leaf." | "Hardware: " + if(BLE_DOOR_HARDWARE_SPECIFICATION_TXT<>"",BLE_DOOR_HARDWARE_SPECIFICATION_TXT,"TBC") + ". FRR: " + if(FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN<>"",FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN+"min","N/A") + ". Security grade: " + if(BLE_DOOR_SECURITY_GRADE_TXT<>"",BLE_DOOR_SECURITY_GRADE_TXT,"N/A") + ". Glazing: " + if(BLE_DOOR_GLAZING_PCT<>"",BLE_DOOR_GLAZING_PCT+"%","N/A") + "." | "Accessibility: " + if(RGL_ACCESS_CLEAR_WIDTH_MM<>"",RGL_ACCESS_CLEAR_WIDTH_MM+"mm clear","N/A") + ". Braille sign: " + if(RGL_ACCESS_BRAILLE_SIGN_BOOL<>"",RGL_ACCESS_BRAILLE_SIGN_BOOL,"N/A") + ". Unit cost: " + if(CST_S_UNIT_RATE_UGX_NR<>"",CST_S_UNIT_RATE_UGX_NR+" UGX","TBC") + ". Lead time: " + if(CST_S_LEAD_TIME_WEEKS_NR<>"",CST_S_LEAD_TIME_WEEKS_NR+"wks","TBC") + "." | BLE_DOOR_WIDTH_MM, BLE_DOOR_HEIGHT_MM, BLE_DOOR_OPERATION_TYPE_TXT, BLE_DOOR_MATERIAL_FINISH_TXT | BLE_DOOR_HARDWARE_SPECIFICATION_TXT, FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN, BLE_DOOR_SECURITY_GRADE_TXT, BLE_DOOR_GLAZING_PCT | RGL_ACCESS_CLEAR_WIDTH_MM, RGL_ACCESS_BRAILLE_SIGN_BOOL, CST_S_UNIT_RATE_UGX_NR, CST_S_LEAD_TIME_WEEKS_NR | BLE_DOOR_WIDTH_MM < 900 → [!DOOR < 900mm] FLS_PROT...< 30 → [!FRR < 30] | BOQ-ARCH-Doors (sh.08) Bill No.3: [W]x[H]mm [OP] door | BOQ-ARCH-Doors | IMMEDIATE
Windows | ARCH | ARCH_TAG_7_PARA_WIN_TXT | ARCH_Win_Para.rfa | if(BLE_WINDOW_WIDTH_MM<>"",BLE_WINDOW_WIDTH_MM,"?") + "x" + if(BLE_WINDOW_HEIGHT_MM<>"",BLE_WINDOW_HEIGHT_MM,"?") + "mm " + if(BLE_WINDOW_OPERATION_TYPE_TXT<>"",BLE_WINDOW_OPERATION_TYPE_TXT,"") + " window. Frame: " + if(BLE_WINDOW_FRAME_MAT_TXT<>"",BLE_WINDOW_FRAME_MAT_TXT,"TBC") + ". Glazing: " + if(BLE_WINDOW_GLAZING_TYPE_TXT<>"",BLE_WINDOW_GLAZING_TYPE_TXT,"TBC") + "." | "Thermal: U=" + if(PER_THERM_U_VALUE_W_M2K_NR<>"",PER_THERM_U_VALUE_W_M2K_NR+"W/m²K","TBC") + ". SHGC=" + if(BLE_WINDOW_SOLAR_HEAT_GAIN_COEFFICIENT_NR<>"",BLE_WINDOW_SOLAR_HEAT_GAIN_COEFFICIENT_NR,"TBC") + ". VLT=" + if(BLE_WINDOW_VLT_PCT<>"",BLE_WINDOW_VLT_PCT+"%","TBC") + ". Mosquito screen: " + if(BLE_WINDOW_MOSQUITO_SCREEN_BOOL<>"",BLE_WINDOW_MOSQUITO_SCREEN_BOOL,"N/A") + ". Burglar bars: " + if(BLE_WINDOW_BURGLAR_BARS_BOOL<>"",BLE_WINDOW_BURGLAR_BARS_BOOL,"N/A") + "." | "Climate zone: " + if(PER_ENV_CLIMATE_ZONE_TXT<>"",PER_ENV_CLIMATE_ZONE_TXT,"TBC") + ". Shading: " + if(BLE_WINDOW_SHADING_DEVICE_TXT<>"",BLE_WINDOW_SHADING_DEVICE_TXT,"none") + ". Energy rating: " + if(PER_THERM_ENERGY_RATING_TXT<>"",PER_THERM_ENERGY_RATING_TXT,"TBC") + ". KCCA approval: " + if(RGL_KCCA_APPROVAL_TXT<>"",RGL_KCCA_APPROVAL_TXT,"N/A") + "." | BLE_WINDOW_WIDTH_MM, BLE_WINDOW_HEIGHT_MM, BLE_WINDOW_OPERATION_TYPE_TXT, BLE_WINDOW_FRAME_MAT_TXT, BLE_WINDOW_GLAZING_TYPE_TXT | PER_THERM_U_VALUE_W_M2K_NR, BLE_WINDOW_SOLAR_HEAT_GAIN_COEFFICIENT_NR, BLE_WINDOW_VLT_PCT, BLE_WINDOW_MOSQUITO_SCREEN_BOOL, BLE_WINDOW_BURGLAR_BARS_BOOL | PER_ENV_CLIMATE_ZONE_TXT, BLE_WINDOW_SHADING_DEVICE_TXT, PER_THERM_ENERGY_RATING_TXT, RGL_KCCA_APPROVAL_TXT | BLE_WINDOW_U_VALUE > 3.00 → [!U > 3.00] BLE_WINDOW_SHGC > 0.40 → [!SHGC > 0.40] | BOQ-ARCH-Windows (sh.08) Bill No.3: [W]x[H]mm [OP] window | BOQ-ARCH-Windows | IMMEDIATE
Rooms/Spaces | ARCH | ARCH_TAG_7_PARA_ROOM_TXT | ARCH_Room_Para.rfa | if(BLE_ROOM_NAME_TXT<>"",BLE_ROOM_NAME_TXT,"Room") + " " + if(ASS_ROOM_NUMBER_TXT<>"",ASS_ROOM_NUMBER_TXT,"") + " ¦ Dept: " + if(ASS_ROOM_DEPARTMENT_TXT<>"",ASS_ROOM_DEPARTMENT_TXT,"TBC") + " ¦ Area: " + if(ASS_ROOM_AREA_SQ_M<>"",ASS_ROOM_AREA_SQ_M+"m²","TBC") + " ¦ Occupancy: " + if(BLE_ROOM_OCCUPANCY_NR<>"",BLE_ROOM_OCCUPANCY_NR+" persons","TBC") + "." | "Design lux: " + if(ASS_DESIGN_LTG_LVL_LUX_NR<>"",ASS_DESIGN_LTG_LVL_LUX_NR+"lux","TBC") + ". Ventilation: " + if(ASS_DESIGN_VENT_RATE_L_S_P<>"",ASS_DESIGN_VENT_RATE_L_S_P+"L/s/person","TBC") + ". Background noise: " + if(PER_ACOUSTICS_BACKGROUND_NOISE_DB<>"",PER_ACOUSTICS_BACKGROUND_NOISE_DB+"dB","TBC") + ". Thermal zone: " + if(BLE_ROOM_THERMAL_ZONE_TXT<>"",BLE_ROOM_THERMAL_ZONE_TXT,"TBC") + "." | "Accessibility: " + if(RGL_ACCESS_CLEAR_WIDTH_MM<>"",RGL_ACCESS_CLEAR_WIDTH_MM+"mm","TBC") + ". Hearing loop: " + if(RGL_ACCESS_HEARING_LOOP_BOOL<>"",RGL_ACCESS_HEARING_LOOP_BOOL,"N/A") + ". Refuge area: " + if(FLS_PROT_REFUGE_AREA_BOOL<>"",FLS_PROT_REFUGE_AREA_BOOL,"N/A") + ". Humidity: " + if(PER_ENV_HUMIDITY_PCT<>"",PER_ENV_HUMIDITY_PCT+"%","TBC") + ". Termite protection: " + if(PER_ENV_TERMITE_PROTECTION_TXT<>"",PER_ENV_TERMITE_PROTECTION_TXT,"N/A") + "." | BLE_ROOM_NAME_TXT, ASS_ROOM_NUMBER_TXT, ASS_ROOM_DEPARTMENT_TXT, ASS_ROOM_AREA_SQ_M, BLE_ROOM_OCCUPANCY_NR | ASS_DESIGN_LTG_LVL_LUX_NR, ASS_DESIGN_VENT_RATE_L_S_P, PER_ACOUSTICS_BACKGROUND_NOISE_DB, BLE_ROOM_THERMAL_ZONE_TXT | RGL_ACCESS_CLEAR_WIDTH_MM, RGL_ACCESS_HEARING_LOOP_BOOL, FLS_PROT_REFUGE_AREA_BOOL, PER_ENV_HUMIDITY_PCT, PER_ENV_TERMITE_PROTECTION_TXT | ASS_DESIGN_LTG_LVL_LUX_NR < 300 → [!LUX < 300] PER_ACOUSTICS_BACKGROUND_NOISE_DB > 40 → [!NOISE > 40dB] | N/A (space, not BOQ item) Room schedule export | BOQ-ARCH-Rooms (space schedule) | IMMEDIATE
STRUCTURAL CATEGORIES
Str. Foundations | STR | STR_TAG_7_PARA_FDN_TXT | STR_Fdn_Para.rfa | if(BLE_STRUCT_FOUNDATION_TYPE_TXT<>"",BLE_STRUCT_FOUNDATION_TYPE_TXT,"Foundation") + " " + if(BLE_STRUCT_FOUNDATION_SZ_TXT<>"",BLE_STRUCT_FOUNDATION_SZ_TXT,"(size TBC)") + ". Concrete: " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"grade TBC") + ". Reinforcement: " + if(BLE_STRUCT_REINFORCEMENT_TXT<>"",BLE_STRUCT_REINFORCEMENT_TXT,"TBC") + "." | "Bearing capacity: " + if(BLE_STRUCT_BEARING_KPA<>"",BLE_STRUCT_BEARING_KPA+"kPa","TBC") + ". Admixture: " + if(CST_TAG_7_PARA_CONCRETE_TXT<>"",CST_TAG_7_PARA_CONCRETE_TXT,"none specified") + ". DPC: " + if(BLE_STRUCT_DPC_TXT<>"",BLE_STRUCT_DPC_TXT,"TBC") + "." | "Insecticide: " + if(PER_ENV_INSECTICIDE_TXT<>"",PER_ENV_INSECTICIDE_TXT,"N/A") + ". Standard: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"N/A") + ". QA: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"TBC") + "." | BLE_STRUCT_FOUNDATION_TYPE_TXT, BLE_STRUCT_FOUNDATION_SZ_TXT, BLE_STRUCT_CONCRETE_GRADE_TXT, BLE_STRUCT_REINFORCEMENT_TXT | BLE_STRUCT_BEARING_KPA, CST_TAG_7_PARA_CONCRETE_TXT, BLE_STRUCT_DPC_TXT | PER_ENV_INSECTICIDE_TXT, RGL_STD_TXT, ASS_QA_CERT_TXT | BLE_STRUCT_CONCRETE_GRADE_TXT check vs exposure class → [!CHECK GRADE] | BOQ-STR-Foundations (sh.08) Bill No.2/3: [SZ] foundation [GRADE] | BOQ-STR-Foundations | HIGH
Str. Columns | STR | STR_TAG_7_PARA_COL_TXT | STR_Col_Para.rfa | if(BLE_STRUCT_COLUMN_SZ_TXT<>"",BLE_STRUCT_COLUMN_SZ_TXT,"(size TBC)") + " RC column. Concrete: " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"grade TBC") + ". Rebar: " + if(BLE_STRUCT_REINFORCEMENT_TXT<>"",BLE_STRUCT_REINFORCEMENT_TXT,"TBC") + "." | "Cover: " + if(BLE_STRUCT_COVER_MM<>"",BLE_STRUCT_COVER_MM+"mm","TBC") + ". Formwork: " + if(BLE_STRUCT_FORMWORK_TXT<>"",BLE_STRUCT_FORMWORK_TXT,"TBC") + ". Fire protection: " + if(FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN<>"",FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN+"min","N/A") + "." | "Standard: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"N/A") + ". Cube test: " + if(ASS_QA_CUBE_TEST_TXT<>"",ASS_QA_CUBE_TEST_TXT,"TBC") + "." | BLE_STRUCT_COLUMN_SZ_TXT, BLE_STRUCT_CONCRETE_GRADE_TXT, BLE_STRUCT_REINFORCEMENT_TXT | BLE_STRUCT_COVER_MM, BLE_STRUCT_FORMWORK_TXT, FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN | RGL_STD_TXT, ASS_QA_CUBE_TEST_TXT | BLE_STRUCT_CONCRETE_GRADE_TXT check → [!CHECK GRADE vs EXPOSURE] | BOQ-STR-Columns (sh.08) Bill No.3: [SZ] RC column [GRADE] | BOQ-STR-Columns | HIGH
Str. Framing | STR | STR_TAG_7_PARA_BEAM_TXT | STR_Beam_Para.rfa | if(BLE_STRUCT_BEAM_SZ_TXT<>"",BLE_STRUCT_BEAM_SZ_TXT,"(size TBC)") + " " + if(BLE_STRUCT_STEEL_GRADE_TXT<>"",BLE_STRUCT_STEEL_GRADE_TXT,"RC") + " beam/slab. Grade: " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"TBC") + "." | "Cover: " + if(BLE_STRUCT_COVER_MM<>"",BLE_STRUCT_COVER_MM+"mm","TBC") + ". Rebar: " + if(BLE_STRUCT_REINFORCEMENT_TXT<>"",BLE_STRUCT_REINFORCEMENT_TXT,"TBC") + ". Steel section: " + if(BLE_STRUCT_STEEL_SECTION_TXT<>"",BLE_STRUCT_STEEL_SECTION_TXT,"N/A") + "." | "FRR: " + if(FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN<>"",FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN+"min","N/A") + ". Standard: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"N/A") + "." | BLE_STRUCT_BEAM_SZ_TXT, BLE_STRUCT_STEEL_GRADE_TXT, BLE_STRUCT_CONCRETE_GRADE_TXT | BLE_STRUCT_COVER_MM, BLE_STRUCT_REINFORCEMENT_TXT, BLE_STRUCT_STEEL_SECTION_TXT | FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN, RGL_STD_TXT | BLE_STRUCT_CONCRETE_GRADE_TXT check → [!CHECK GRADE] | BOQ-STR-Beams (sh.08) Bill No.3: [SZ] RC/steel beam | BOQ-STR-Beams | HIGH
Stairs | ARCH | ARCH_TAG_7_PARA_STAIR_TXT | ARCH_Stair_Para.rfa | if(BLE_STAIR_MAT_TXT<>"",BLE_STAIR_MAT_TXT,"") + " stair, " + if(BLE_STAIR_RISE_MM<>"",BLE_STAIR_RISE_MM+"mm","?mm") + " rise, " + if(BLE_STAIR_GOING_MM<>"",BLE_STAIR_GOING_MM+"mm","?mm") + " going, " + if(BLE_STAIR_WIDTH_MM<>"",BLE_STAIR_WIDTH_MM+"mm","?mm") + " wide. Tread: " + if(BLE_STAIR_TREAD_FINISH_TXT<>"",BLE_STAIR_TREAD_FINISH_TXT,"TBC") + ". Handrail: " + if(BLE_STAIR_HANDRAIL_MAT_TXT<>"",BLE_STAIR_HANDRAIL_MAT_TXT,"TBC") + "." | "Nosing: " + if(BLE_STAIR_NOSING_TXT<>"",BLE_STAIR_NOSING_TXT,"TBC") + ". Balustrade: " + if(BLE_STAIR_BALUSTRADE_SPEC_TXT<>"",BLE_STAIR_BALUSTRADE_SPEC_TXT,"TBC") + ". FRR: " + if(FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN<>"",FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN+"min","N/A") + "." | "Reg: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"N/A") + ". PWD compliant: " + if(RGL_ACCESS_CLEAR_WIDTH_MM<>"",RGL_ACCESS_CLEAR_WIDTH_MM+"mm clear","N/A") + ". Cost: " + if(CST_S_UNIT_RATE_UGX_NR<>"",CST_S_UNIT_RATE_UGX_NR+" UGX/flight","TBC") + "." | BLE_STAIR_MAT_TXT, BLE_STAIR_RISE_MM, BLE_STAIR_GOING_MM, BLE_STAIR_WIDTH_MM, BLE_STAIR_TREAD_FINISH_TXT, BLE_STAIR_HANDRAIL_MAT_TXT | BLE_STAIR_NOSING_TXT, BLE_STAIR_BALUSTRADE_SPEC_TXT, FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN | RGL_STD_TXT, RGL_ACCESS_CLEAR_WIDTH_MM, CST_S_UNIT_RATE_UGX_NR | RISE < 150 or > 190 → [!RISE] GOING < 250 or > 400 → [!GOING] WIDTH < 1000 → [!WIDTH < 1000] | BOQ-ARCH-Stairs (sh.08) Bill No.3: [MAT] stair [W]mm wide | BOQ-ARCH-Stairs | HIGH
Ramps | ARCH | ARCH_TAG_7_PARA_RAMP_TXT | ARCH_Ramp_Para.rfa | "Ramp at " + if(BLE_RAMP_SLOPE_PCT<>"",BLE_RAMP_SLOPE_PCT+"%","?%") + " gradient, " + if(BLE_RAMP_SURFACE_FINISH_TXT<>"",BLE_RAMP_SURFACE_FINISH_TXT,"surface TBC") + " finish. Handrails: " + if(BLE_RAMP_HANDRAIL_BOTH_SIDES_BOOL<>"",BLE_RAMP_HANDRAIL_BOTH_SIDES_BOOL,"TBC") + ". Clear width: " + if(RGL_ACCESS_CLEAR_WIDTH_MM<>"",RGL_ACCESS_CLEAR_WIDTH_MM+"mm","TBC") + "." | "Landing: " + if(BLE_RAMP_LANDING_DIM_TXT<>"",BLE_RAMP_LANDING_DIM_TXT,"TBC") + ". Handrail height: " + if(BLE_RAMP_HANDRAIL_HGT_MM<>"",BLE_RAMP_HANDRAIL_HGT_MM+"mm","TBC") + ". Non-slip: " + if(BLE_RAMP_NONSLIP_TREATMENT_TXT<>"",BLE_RAMP_NONSLIP_TREATMENT_TXT,"TBC") + "." | "Uganda PWD Act 2020 compliance. Max gradient 1:12 (8.33%). Max run 9m. Approval: " + if(RGL_KCCA_APPROVAL_TXT<>"",RGL_KCCA_APPROVAL_TXT,"pending") + "." | BLE_RAMP_SLOPE_PCT, BLE_RAMP_SURFACE_FINISH_TXT, BLE_RAMP_HANDRAIL_BOTH_SIDES_BOOL, RGL_ACCESS_CLEAR_WIDTH_MM | BLE_RAMP_LANDING_DIM_TXT, BLE_RAMP_HANDRAIL_HGT_MM, BLE_RAMP_NONSLIP_TREATMENT_TXT | RGL_KCCA_APPROVAL_TXT | SLOPE > 8.33 → [!SLOPE > 1:12] WIDTH < 900 → [!WIDTH < 900mm] | BOQ-ARCH-Ramps (sh.08) Bill No.3: Ramp at [SLOPE]% | BOQ-ARCH-Ramps | HIGH
Curtain Panels | ARCH | ARCH_TAG_7_PARA_FACADE_TXT | ARCH_Facade_Para.rfa | if(BLE_FACADE_CLR_TXT<>"",BLE_FACADE_CLR_TXT,"") + " " + if(BLE_FACADE_FINISH_TXT<>"",BLE_FACADE_FINISH_TXT,"") + " curtain panel, " + if(BLE_FACADE_FIX_SYSTEM_TXT<>"",BLE_FACADE_FIX_SYSTEM_TXT,"fixing TBC") + " fixing. Glass: " + if(BLE_FACADE_GLASS_TYPE_TXT<>"",BLE_FACADE_GLASS_TYPE_TXT,"TBC") + ". U: " + if(PER_THERM_U_VALUE_W_M2K_NR<>"",PER_THERM_U_VALUE_W_M2K_NR+"W/m²K","TBC") + "." | "Panel size: " + if(BLE_FACADE_PANEL_WIDTH_MM<>"",BLE_FACADE_PANEL_WIDTH_MM+"x","?x") + if(BLE_FACADE_PANEL_HEIGHT_MM<>"",BLE_FACADE_PANEL_HEIGHT_MM+"mm","?mm") + ". Insulation: " + if(BLE_FACADE_INSULATION_TXT<>"",BLE_FACADE_INSULATION_TXT,"TBC") + ". Water penetration: " + if(BLE_FACADE_WTR_PENETRATION_TXT<>"",BLE_FACADE_WTR_PENETRATION_TXT,"TBC") + "." | "Energy rating: " + if(PER_THERM_ENERGY_RATING_TXT<>"",PER_THERM_ENERGY_RATING_TXT,"TBC") + ". KCCA/UNBS approval: " + if(RGL_KCCA_APPROVAL_TXT<>"",RGL_KCCA_APPROVAL_TXT,"pending") + ". EPD: " + if(MAT_EPD_REF_TXT<>"",MAT_EPD_REF_TXT,"N/A") + "." | BLE_FACADE_CLR_TXT, BLE_FACADE_FINISH_TXT, BLE_FACADE_FIX_SYSTEM_TXT, BLE_FACADE_GLASS_TYPE_TXT, PER_THERM_U_VALUE_W_M2K_NR | BLE_FACADE_PANEL_WIDTH_MM, BLE_FACADE_PANEL_HEIGHT_MM, BLE_FACADE_INSULATION_TXT, BLE_FACADE_WTR_PENETRATION_TXT | PER_THERM_ENERGY_RATING_TXT, RGL_KCCA_APPROVAL_TXT, MAT_EPD_REF_TXT | PER_THERM_U_VALUE > 2.20 → [!U > 2.20 FACADE] | BOQ-ARCH-CurtainWall (sh.08) Bill No.3: [CLR] [FINISH] panel [W]x[H] | BOQ-ARCH-CurtainWall | HIGH
Casework | ARCH | ARCH_TAG_7_PARA_CASEWORK_TXT | ARCH_Case_Para.rfa | "This " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"casework unit") + ". By " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"TBC") + " model " + if(ASS_MODEL_NR_TXT<>"",ASS_MODEL_NR_TXT,"TBC") + "." | "Material: " + if(BLE_CASE_MAT_TXT<>"",BLE_CASE_MAT_TXT,"TBC") + ". Finish: " + if(BLE_CASE_FINISH_TXT<>"",BLE_CASE_FINISH_TXT,"TBC") + ". FRR: " + if(FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN<>"",FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN+"min","N/A") + "." | "Material spec: " + if(BLE_CSWORK_MAT_TXT<>"",BLE_CSWORK_MAT_TXT,"TBC") + ". Finish: " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"TBC") + ". Lead time: " + if(ASS_LEAD_TIME_TXT<>"",ASS_LEAD_TIME_TXT,"TBC") + ". Standard: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"N/A") + "." | ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT, ASS_MODEL_NR_TXT | BLE_CASE_MAT_TXT, BLE_CASE_FINISH_TXT, FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN | BLE_CSWORK_MAT_TXT, ASS_LEAD_TIME_TXT, RGL_STD_TXT | ASS_MANUFACTURER_TXT absent → flag for procurement review | BOQ-ARCH-Casework (sh.08) Bill No.3: [DESC] casework | BOQ-ARCH-Casework | MEDIUM
Furniture | ARCH | ARCH_TAG_7_PARA_FURNITURE_TXT | ARCH_Furn_Para.rfa | "This " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"furniture item") + ". By " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"TBC") + " model " + if(ASS_MODEL_NR_TXT<>"",ASS_MODEL_NR_TXT,"TBC") + ". Status: " + if(ASS_STATUS_TXT<>"",ASS_STATUS_TXT,"TBC") + "." | "Qty: " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"TBC") + ". Material: " + if(BLE_FURN_MAT_TXT<>"",BLE_FURN_MAT_TXT,"TBC") + ". Finish: " + if(BLE_FURN_FINISH_TXT<>"",BLE_FURN_FINISH_TXT,"TBC") + ". By: " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"TBC") + "." | "Cost: " + if(ASS_CST_TOTAL_UGX_NR<>"",ASS_CST_TOTAL_UGX_NR+" UGX","TBC") + ". Warranty: " + if(ASS_WARRANTY_TXT<>"",ASS_WARRANTY_TXT,"TBC") + "." | ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT, ASS_MODEL_NR_TXT, ASS_STATUS_TXT | BLE_ROOM_NAME_TXT, ASS_QTY_NR | ASS_CST_TOTAL_UGX_NR, ASS_WARRANTY_TXT | No automated threshold — furniture is non-performance element | N/A (FF&E schedule) Export to FF&E schedule | FF&E-Schedule | MEDIUM
MEP — HVAC
Mech. Equipment | HVAC | HVC_TAG_7_PARA_SPEC_TXT | HVAC_Eqp_Para.rfa | "" + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"HVAC equipment") + ". Capacity: " + if(HVC_CAP_KW<>"",HVC_CAP_KW+"kW","TBC") + ". Refrigerant: " + if(HVC_REFRIGERANT_TXT<>"",HVC_REFRIGERANT_TXT,"TBC") + ". Power: " + if(HVC_PWR_KW<>"",HVC_PWR_KW+"kW","TBC") + ". COP/EER: " + if(HVC_EFF_RATIO_NR<>"",HVC_EFF_RATIO_NR,"TBC") + ". " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"") + " " + if(ASS_MODEL_NR_TXT<>"",ASS_MODEL_NR_TXT,"") + "." | "BMS control: " + if(HVC_BMS_CONTROL_TYPE_TXT<>"",HVC_BMS_CONTROL_TYPE_TXT,"TBC") + ". Mount height: " + if(MNT_HGT_MM<>"",MNT_HGT_MM+"mm","TBC") + ". Voltage: " + if(HVC_VLT_V<>"",HVC_VLT_V+"V","TBC") + ". Phases: " + if(ELC_PNL_PHS_COUNT_NR<>"",ELC_PNL_PHS_COUNT_NR+"Ph","TBC") + "." | "Install detail: " + if(ASS_INST_DETAIL_NUM_TXT<>"",ASS_INST_DETAIL_NUM_TXT,"TBC") + ". Commissioning: " + if(ASS_COMMISSION_REQ_TXT<>"",ASS_COMMISSION_REQ_TXT,"TBC") + ". QA cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"TBC") + ". Inspect freq: " + if(ASS_INSPECT_FREQ_TXT<>"",ASS_INSPECT_FREQ_TXT,"TBC") + "." | ASS_DESCRIPTION_TXT, HVC_CAP_KW, HVC_REFRIGERANT_TXT, HVC_PWR_KW, HVC_EFF_RATIO_NR, ASS_MANUFACTURER_TXT, ASS_MODEL_NR_TXT | HVC_BMS_CONTROL_TYPE_TXT, MNT_HGT_MM, HVC_VLT_V, ELC_PNL_PHS_COUNT_NR | ASS_INST_DETAIL_NUM_TXT, ASS_COMMISSION_REQ_TXT, ASS_QA_CERT_TXT, ASS_INSPECT_FREQ_TXT | HVC_EFF_RATIO_NR < 3.0 → [!EFF < 3.0 COP] | BOQ-HVC-Equipment (sh.08) (sh.08) Bill No.7: [CAP]kW [MODEL] [TYPE] AC | BOQ-HVAC-Equipment | IMMEDIATE
Ducts | HVAC | HVC_TAG_7_PARA_DUCT_TXT | HVAC_Duct_Para.rfa | if(HVC_DUCT_CLASS_TXT<>"",HVC_DUCT_CLASS_TXT,"") + "-class " + if(HVC_DCT_MAT_TXT<>"",HVC_DCT_MAT_TXT,"GI") + " duct " + if(HVC_DCT_WIDTH_MM<>"",HVC_DCT_WIDTH_MM+"x","") + if(HVC_DCT_HEIGHT_MM<>"",HVC_DCT_HEIGHT_MM+"mm ","") + if(HVC_DCT_DIA_MM<>"","DN"+HVC_DCT_DIA_MM+" ","") + ". Lining: " + if(HVC_DUCT_LINING_TXT<>"",HVC_DUCT_LINING_TXT,"none") + ". Flow: " + if(HVC_DCT_FLW_CFM<>"",HVC_DCT_FLW_CFM+"CFM","TBC") + "." | "Velocity: " + if(HVC_VEL_MPS<>"",HVC_VEL_MPS+"m/s","TBC") + ". Insulation: " + if(HVC_DCT_INSULATION_TXT<>"",HVC_DCT_INSULATION_TXT,"TBC") + ". Leakage class: " + if(HVC_DUCT_LEAKAGE_CLASS_TXT<>"",HVC_DUCT_LEAKAGE_CLASS_TXT,"TBC") + "." | "System: " + if(ASS_SYSTEM_TYPE_TXT<>"",ASS_SYSTEM_TYPE_TXT,"TBC") + ". Zone: " + if(ASS_ZONE_TXT<>"",ASS_ZONE_TXT,"TBC") + ". Hangers at: " + if(HVC_DCT_HANGER_SPACING_MM<>"",HVC_DCT_HANGER_SPACING_MM+"mm","TBC") + "." | HVC_DUCT_CLASS_TXT, HVC_DCT_MAT_TXT, HVC_DCT_WIDTH_MM, HVC_DCT_HEIGHT_MM, HVC_DCT_DIA_MM, HVC_DUCT_LINING_TXT, HVC_DCT_FLW_CFM | HVC_VEL_MPS, HVC_DCT_INSULATION_TXT, HVC_DUCT_LEAKAGE_CLASS_TXT | ASS_SYSTEM_TYPE_TXT, ASS_ZONE_TXT, HVC_DCT_HANGER_SPACING_MM | HVC_VEL_MPS > 6.0 → [!VEL > 6.0m/s] | BOQ-HVAC-Ductwork (sh.08) Bill No.7: [CLASS]-class [MAT] duct [W]x[H] | BOQ-HVAC-Ductwork | IMMEDIATE
Flex Ducts | HVAC | HVC_TAG_7_PARA_FLEXDUCT_TXT | HVAC_FlxDuct_Para.rfa | "Flexible " + if(HVC_DCT_MAT_TXT<>"",HVC_DCT_MAT_TXT,"") + " duct " + if(HVC_DCT_DIA_MM<>"","DN"+HVC_DCT_DIA_MM,"size TBC") + ", " + if(HVC_DUCT_LINING_TXT<>"",HVC_DUCT_LINING_TXT,"") + " lining. Velocity: " + if(HVC_VEL_MPS<>"",HVC_VEL_MPS+"m/s","TBC") + "." | "Flow: " + if(HVC_DCT_FLW_CFM<>"",HVC_DCT_FLW_CFM+"CFM","TBC") + ". Connection: " + if(HVC_DCT_CONNECTION_TXT<>"",HVC_DCT_CONNECTION_TXT,"TBC") + "." | "Standard: SMACNA max 1500mm. Install leak class: " + if(HVC_DUCT_CLASS_TXT<>"",HVC_DUCT_CLASS_TXT,"Class B") + ". Commissioning test date: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"TBC") + ". Lining: " + if(HVC_DCT_LINING_TXT<>"",HVC_DCT_LINING_TXT,"acoustic") + "." | HVC_DCT_MAT_TXT, HVC_DCT_DIA_MM, HVC_DUCT_LINING_TXT, HVC_VEL_MPS | HVC_DCT_FLW_CFM, HVC_DCT_CONNECTION_TXT | HVC_DUCT_CLASS_TXT, ASS_QA_CERT_TXT, HVC_DCT_LINING_TXT | HVC_VEL_MPS > 4.0 → [!FLEX VEL > 4.0m/s] (stricter than rigid) | BOQ-HVC-FlexDucts (sh.08) (sh.08) Bill No.7: [DIA]mm flexible duct | BOQ-HVAC-FlexDucts | HIGH
Air Terminals | HVAC | HVC_TAG_7_PARA_AT_TXT | HVAC_AT_Para.rfa | if(HVC_TERMINAL_TYPE_TXT<>"",HVC_TERMINAL_TYPE_TXT,"Air terminal") + " " + if(HVC_DCT_TERMINAL_SZ_TXT<>"",HVC_DCT_TERMINAL_SZ_TXT,"(size TBC)") + ". Flow: " + if(HVC_DCT_FLW_CFM<>"",HVC_DCT_FLW_CFM+"CFM","TBC") + ". Sound: " + if(HVC_DCT_TERMINAL_SOUND_DB_NR<>"",HVC_DCT_TERMINAL_SOUND_DB_NR+"dB","TBC") + "." | "Neck: " + if(HVC_DCT_NECK_SZ_TXT<>"",HVC_DCT_NECK_SZ_TXT,"TBC") + ". Pressure drop: " + if(HVC_TERMINAL_PD_PA<>"",HVC_TERMINAL_PD_PA+"Pa","TBC") + ". Damper: " + if(HVC_TERMINAL_DAMPER_BOOL<>"",HVC_TERMINAL_DAMPER_BOOL,"TBC") + "." | "By " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"TBC") + ". System: " + if(ASS_SYSTEM_TYPE_TXT<>"",ASS_SYSTEM_TYPE_TXT,"TBC") + "." | HVC_TERMINAL_TYPE_TXT, HVC_DCT_TERMINAL_SZ_TXT, HVC_DCT_FLW_CFM, HVC_DCT_TERMINAL_SOUND_DB_NR | HVC_DCT_NECK_SZ_TXT, HVC_TERMINAL_PD_PA, HVC_TERMINAL_DAMPER_BOOL | ASS_MANUFACTURER_TXT, ASS_SYSTEM_TYPE_TXT | HVC_DCT_TERMINAL_SOUND_DB_NR > 35 → [!NOISE > 35dB] | BOQ-HVAC-AirTerminals (sh.08) Bill No.7: [TYPE] terminal [SZ] [FLOW]m³/h | BOQ-HVAC-AirTerminals | IMMEDIATE
Duct Accessories | HVAC | HVC_TAG_7_PARA_DCTACC_TXT | HVAC_DctAcc_Para.rfa | "This " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"duct accessory") + ", " + if(HVC_DCT_MAT_TXT<>"",HVC_DCT_MAT_TXT,"TBC") + " body. Control: " + if(HVC_CONTROL_TYPE_TXT<>"",HVC_CONTROL_TYPE_TXT,"none") + ". By " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"TBC") + "." | "Actuator: " + if(HVC_ACTUATOR_TXT<>"",HVC_ACTUATOR_TXT,"TBC") + ". FRR: " + if(FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN<>"",FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN+"min","N/A") + "." | "Test cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"pending") + ". Standard: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"SMACNA/CIBSE") + ". Inspection interval: " + if(ASS_INSPECT_FREQ_TXT<>"",ASS_INSPECT_FREQ_TXT,"annual") + "." | ASS_DESCRIPTION_TXT, HVC_DCT_MAT_TXT, HVC_CONTROL_TYPE_TXT, ASS_MANUFACTURER_TXT | HVC_ACTUATOR_TXT, FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN | ASS_QA_CERT_TXT, RGL_STD_TXT, ASS_INSPECT_FREQ_TXT | FRR < 30 on fire dampers → [!FRR < 30] | BOQ-HVC-DuctAcc (sh.08) (sh.08) Bill No.7: [DESC] accessory | BOQ-HVAC-DuctAcc | HIGH
MEP — ELECTRICAL
Elec. Equipment (DB Panels) | ELEC | ELC_TAG_7_PARA_PANEL_TXT | ELC_Panel_Para.rfa | if(ELC_PNL_DESIGNATION_NAME_TXT<>"",ELC_PNL_DESIGNATION_NAME_TXT,"DB") + " distribution board. " + if(ELC_PNL_VLT_V<>"",ELC_PNL_VLT_V+"V","") + " " + if(ELC_PNL_PHS_COUNT_NR<>"",ELC_PNL_PHS_COUNT_NR+"-phase","") + ", " + if(ELC_PNL_NUM_OF_WAYS_NR<>"",ELC_PNL_NUM_OF_WAYS_NR+" ways","?W") + ". Main: " + if(ELC_PNL_MAIN_BRK_A<>"",ELC_PNL_MAIN_BRK_A+"A","TBC") + ". Fault: " + if(ELC_PNL_SHORT_CIRCUIT_KA<>"",ELC_PNL_SHORT_CIRCUIT_KA+"kA","TBC") + "." | "Load: " + if(ELC_PNL_CONNECTED_LOAD_KW<>"",ELC_PNL_CONNECTED_LOAD_KW+"kW","TBC") + "/" + if(ELC_PNL_RATED_KW<>"",ELC_PNL_RATED_KW+"kW rated","TBC") + ". Spare ways: " + if(ELC_PNL_SPARE_WAYS_NR<>"",ELC_PNL_SPARE_WAYS_NR,"TBC") + ". IP rating: " + if(ELC_PNL_IP_RATING_TXT<>"",ELC_PNL_IP_RATING_TXT,"TBC") + ". Feeder cable: " + if(ELC_CBL_FEEDER_SZ_MM2<>"",ELC_CBL_FEEDER_SZ_MM2+"mm²","TBC") + "." | "UMEME approval: " + if(RGL_UMEME_APPROVAL_TXT<>"",RGL_UMEME_APPROVAL_TXT,"pending") + ". KCCA: " + if(RGL_KCCA_APPROVAL_TXT<>"",RGL_KCCA_APPROVAL_TXT,"pending") + ". NEMA: " + if(RGL_NEMA_APPROVAL_TXT<>"",RGL_NEMA_APPROVAL_TXT,"N/A") + ". Test report: " + if(ASS_QA_TEST_REPORT_TXT<>"",ASS_QA_TEST_REPORT_TXT,"TBC") + "." | ELC_PNL_DESIGNATION_NAME_TXT, ELC_PNL_VLT_V, ELC_PNL_PHS_COUNT_NR, ELC_PNL_NUM_OF_WAYS_NR, ELC_PNL_MAIN_BRK_A, ELC_PNL_SHORT_CIRCUIT_KA | ELC_PNL_CONNECTED_LOAD_KW, ELC_PNL_RATED_KW, ELC_PNL_SPARE_WAYS_NR, ELC_PNL_IP_RATING_TXT, ELC_CBL_FEEDER_SZ_MM2 | RGL_UMEME_APPROVAL_TXT, RGL_KCCA_APPROVAL_TXT, RGL_NEMA_APPROVAL_TXT, ASS_QA_TEST_REPORT_TXT | ELC_VLT_DROP_PCT > 4.0 → [!VD > 4%] ELC_PNL_CONNECTED_LOAD > 80% rated → [!OVERLOADED] ELC_PNL_SC < 6kA → [!SC < 6kA] | BOQ-ELC-DBPanels (sh.08) Bill No.4: [DESIGN] DB [V][PH] [WAYS]W | BOQ-ELC-DBPanels | IMMEDIATE
Lighting Fixtures | ELEC | LTG_TAG_7_PARA_SPEC_TXT | LTG_Fix_Para.rfa | if(LTG_FIX_TYPE_CLASSIFICATION_TXT<>"",LTG_FIX_TYPE_CLASSIFICATION_TXT,"Luminaire") + " " + if(LTG_FIX_LMP_WATTAGE_W<>"",LTG_FIX_LMP_WATTAGE_W+"W","?W") + " LED, " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"") + ". Mounting: " + if(LTG_FIX_MOUNTING_TXT<>"",LTG_FIX_MOUNTING_TXT,"TBC") + ". By " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"TBC") + " (Type " + if(ASS_EQUIPMENT_TAG_TXT<>"",ASS_EQUIPMENT_TAG_TXT,"?") + ")." | "Efficacy: " + if(LTG_EFFICACY_LM_W<>"",LTG_EFFICACY_LM_W+"lm/W","TBC") + ". CRI: " + if(LTG_CLR_CRI_NR<>"",LTG_CLR_CRI_NR,"TBC") + ". CCT: " + if(LTG_CLR_CCT_K_NR<>"",LTG_CLR_CCT_K_NR+"K","TBC") + ". IP: " + if(LTG_FIX_IP_RATING_TXT<>"",LTG_FIX_IP_RATING_TXT,"TBC") + ". Control: " + if(LTG_FIX_CTRL_INTERFACE_TXT<>"",LTG_FIX_CTRL_INTERFACE_TXT,"TBC") + "." | "Emergency: " + if(LTG_FIX_EMERGENCY_BOOL<>"",LTG_FIX_EMERGENCY_BOOL,"N/A") + ". DALI: " + if(LTG_FIX_DALI_BOOL<>"",LTG_FIX_DALI_BOOL,"N/A") + ". Luminaire schedule ref: " + if(ASS_EQUIPMENT_TAG_TXT<>"",ASS_EQUIPMENT_TAG_TXT,"TBC") + ". ELC approved: " + if(RGL_UMEME_APPROVAL_TXT<>"",RGL_UMEME_APPROVAL_TXT,"pending") + "." | LTG_FIX_TYPE_CLASSIFICATION_TXT, LTG_FIX_LMP_WATTAGE_W, ASS_DESCRIPTION_TXT, LTG_FIX_MOUNTING_TXT, ASS_MANUFACTURER_TXT, ASS_EQUIPMENT_TAG_TXT | LTG_EFFICACY_LM_W, LTG_CLR_CRI_NR, LTG_CLR_CCT_K_NR, LTG_FIX_IP_RATING_TXT, LTG_FIX_CTRL_INTERFACE_TXT | LTG_FIX_EMERGENCY_BOOL, LTG_FIX_DALI_BOOL, RGL_UMEME_APPROVAL_TXT | ASS_DESIGN_LTG_LVL_LUX_NR < 300 (room) → [!LUX < 300] | BOQ-ELC-Luminaires (sh.08) Bill No.4: [TYPE] [W]W LED luminaire | BOQ-ELC-Luminaires | IMMEDIATE
Elec. Fixtures (Points & Sockets) | ELEC | ELC_TAG_7_PARA_CIRCUIT_TXT | ELC_Fix_Para.rfa | if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"Electrical fixture") + ". Circuit: " + if(ELC_CKT_CBL_TYPE_TXT<>"",ELC_CKT_CBL_TYPE_TXT,"TBC") + " cable, " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","?mm") + " PVC conduit " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"") + "." | "VD: " + if(ELC_VLT_DROP_PCT<>"",ELC_VLT_DROP_PCT+"%","TBC") + ". Rating: " + if(ELC_CKT_BRK_RATING_A<>"",ELC_CKT_BRK_RATING_A+"A","TBC") + ". DB: " + if(ELC_PNL_DESIGNATION_NAME_TXT<>"",ELC_PNL_DESIGNATION_NAME_TXT,"TBC") + ". By " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"TBC") + "." | "Test cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"TBC") + ". UMEME: " + if(RGL_UMEME_APPROVAL_TXT<>"",RGL_UMEME_APPROVAL_TXT,"pending") + "." | ASS_DESCRIPTION_TXT, ELC_CKT_CBL_TYPE_TXT, ELC_CDT_SZ_MM, ELC_CDT_INSTALL_METHOD_TXT | ELC_VLT_DROP_PCT, ELC_CKT_BRK_RATING_A, ELC_PNL_DESIGNATION_NAME_TXT, ASS_MANUFACTURER_TXT | ASS_QA_CERT_TXT, RGL_UMEME_APPROVAL_TXT | ELC_VLT_DROP_PCT > 4.0 → [!VD > 4%] | BOQ-ELC-Lighting-Points / BOQ-ELC-Socket-Points (sh.08) (sh.08) Bill No.4: Lighting/socket/TV/FA/CCTV points | BOQ-ELC-Points | IMMEDIATE
Conduits | ELEC | ELC_TAG_7_PARA_CONDUIT_TXT | ELC_Cdt_Para.rfa | if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","?mm") + " " + if(ELC_CDT_MAT_TXT<>"",ELC_CDT_MAT_TXT,"PVC") + " conduit, " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"") + " installation. Fill: " + if(ELC_CDT_CBL_FILL_PCT<>"",ELC_CDT_CBL_FILL_PCT+"%","TBC") + "." | "Cable: " + if(ELC_CBL_TYPE_TXT<>"",ELC_CBL_TYPE_TXT,"TBC") + " " + if(ELC_CBL_CORES_NR<>"",ELC_CBL_CORES_NR+"c×","") + if(ELC_CBL_SZ_MM2<>"",ELC_CBL_SZ_MM2+"mm²","TBC") + ". Load current: " + if(ELC_CBL_LOAD_A<>"",ELC_CBL_LOAD_A+"A","TBC") + ". From: " + if(ELC_CBL_SOURCE_TXT<>"",ELC_CBL_SOURCE_TXT,"TBC") + " → " + if(ELC_CBL_DEST_TXT<>"",ELC_CBL_DEST_TXT,"TBC") + "." | "As-installed cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"TBC") + ". RGL: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"IEC 60364") + "." | ELC_CDT_SZ_MM, ELC_CDT_MAT_TXT, ELC_CDT_INSTALL_METHOD_TXT, ELC_CDT_CBL_FILL_PCT | ELC_CBL_TYPE_TXT, ELC_CBL_CORES_NR, ELC_CBL_SZ_MM2, ELC_CBL_LOAD_A, ELC_CBL_SOURCE_TXT, ELC_CBL_DEST_TXT | ASS_QA_CERT_TXT, RGL_STD_TXT | ELC_CDT_CBL_FILL_PCT > 40 → [!CONDUIT FILL > 40%] | BOQ-ELC-Conduits (sh.08) Bill No.4: [SZ]mm [MAT] conduit | BOQ-ELC-Conduits | HIGH
Cable Trays | ELEC | ELC_TAG_7_PARA_TRAY_TXT | ELC_CT_Para.rfa | if(ELC_CTR_WIDTH_MM<>"",ELC_CTR_WIDTH_MM+"x","?x") + if(ELC_CTR_DEPTH_MM<>"",ELC_CTR_DEPTH_MM+"mm","?mm") + " " + if(ELC_CTR_MAT_TXT<>"",ELC_CTR_MAT_TXT,"steel") + " cable tray. Fill: " + if(ELC_CTR_FILL_PCT<>"",ELC_CTR_FILL_PCT+"%","TBC") + "." | "Cable: " + if(ELC_CBL_TYPE_TXT<>"",ELC_CBL_TYPE_TXT,"TBC") + ". Load: " + if(ELC_CBL_LOAD_A<>"",ELC_CBL_LOAD_A+"A","TBC") + ". Support spacing: " + if(ELC_CTR_SUPPORT_SPACING_MM<>"",ELC_CTR_SUPPORT_SPACING_MM+"mm","TBC") + "." | "Standard: IEC 61537. Cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"pending") + ". Earthing: " + if(ELC_EARTH_TXT<>"",ELC_EARTH_TXT,"continuous earth bond required") + ". Inspection: " + if(ASS_INSPECT_FREQ_TXT<>"",ASS_INSPECT_FREQ_TXT,"annual") + "." | ELC_CTR_WIDTH_MM, ELC_CTR_DEPTH_MM, ELC_CTR_MAT_TXT, ELC_CTR_FILL_PCT | ELC_CBL_TYPE_TXT, ELC_CBL_LOAD_A, ELC_CTR_SUPPORT_SPACING_MM | ASS_QA_CERT_TXT, ELC_EARTH_TXT, ASS_INSPECT_FREQ_TXT | ELC_CTR_FILL_PCT > 45 → [!TRAY FILL > 45%] | BOQ-ELC-CableTrays (sh.08) Bill No.4: Steel cable tray [W]x[D]mm | BOQ-ELC-CableTrays | HIGH
MEP — PLUMBING & DRAINAGE
Pipes | PLM | PLM_TAG_7_PARA_PIPE_TXT | PLM_Pipe_Para.rfa | if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm","?mm") + " " + if(PLM_PPE_MAT_TXT<>"",PLM_PPE_MAT_TXT,"pipe") + " pipe " + if(PLM_PPE_PSR_RATING_BAR<>"","PN"+PLM_PPE_PSR_RATING_BAR,"") + " complete with fittings. System: " + if(ASS_SYSTEM_TYPE_TXT<>"",ASS_SYSTEM_TYPE_TXT,"TBC") + "." | "Flow: " + if(PLM_PPE_FLW_LPS<>"",PLM_PPE_FLW_LPS+"L/s","TBC") + ". Velocity: " + if(PLM_VEL_MPS<>"",PLM_VEL_MPS+"m/s","TBC") + ". Pressure: " + if(PLM_PSR_KPA<>"",PLM_PSR_KPA+"kPa","TBC") + ". Insulation: " + if(PLM_PPE_INSULATION_TXT<>"",PLM_PPE_INSULATION_TXT,"none") + "." | "NWSC approval: " + if(RGL_NWSC_APPROVAL_TXT<>"",RGL_NWSC_APPROVAL_TXT,"pending") + ". Test pressure: " + if(PLM_PPE_TEST_PSR_BAR<>"",PLM_PPE_TEST_PSR_BAR+"bar","TBC") + ". Tracer wire: " + if(PLM_PPE_TRACER_WIRE_BOOL<>"",PLM_PPE_TRACER_WIRE_BOOL,"N/A") + "." | PLM_PPE_SZ_MM, PLM_PPE_MAT_TXT, PLM_PPE_PSR_RATING_BAR, ASS_SYSTEM_TYPE_TXT | PLM_PPE_FLW_LPS, PLM_VEL_MPS, PLM_PSR_KPA, PLM_PPE_INSULATION_TXT | RGL_NWSC_APPROVAL_TXT, PLM_PPE_TEST_PSR_BAR, PLM_PPE_TRACER_WIRE_BOOL | PLM_PPE_FLW_LPS > 2.0 → [!FLOW > 2.0] PLM_VEL_MPS > 2.0 → [!VEL > 2.0] PLM_PSR_KPA < 150 or > 600 → [!PSR] | BOQ-PLM-Pipework (sh.08) Bill No.5: [SZ]mm [MAT] pipework | BOQ-PLM-Pipework | IMMEDIATE
Plumbing Fixtures | PLM | PLM_TAG_7_PARA_FIXTURE_TXT | PLM_Fix_Para.rfa | "This " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"sanitary fixture") + ". " + if(PLM_PPE_MAT_TXT<>"",PLM_PPE_MAT_TXT,"") + " body, DN" + if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM,"?") + ". Drain: " + if(PLM_DRN_BODY_MAT_TXT<>"",PLM_DRN_BODY_MAT_TXT,"TBC") + " with " + if(PLM_DRN_TRAP_TYPE_TXT<>"",PLM_DRN_TRAP_TYPE_TXT,"trap TBC") + ". By " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"TBC") + " model " + if(ASS_MODEL_NR_TXT<>"",ASS_MODEL_NR_TXT,"TBC") + "." | "Hot water: " + if(PLM_HOTWTR_TEMP_C<>"",PLM_HOTWTR_TEMP_C+"°C","TBC") + ". Recovery: " + if(PLM_HOTWTR_RECOVERY_L_H<>"",PLM_HOTWTR_RECOVERY_L_H+"L/h","TBC") + ". Flow: " + if(PLM_PPE_FLW_LPS<>"",PLM_PPE_FLW_LPS+"L/s","TBC") + ". Pressure: " + if(PLM_PSR_KPA<>"",PLM_PSR_KPA+"kPa","TBC") + "." | "NWSC approval: " + if(RGL_NWSC_APPROVAL_TXT<>"",RGL_NWSC_APPROVAL_TXT,"pending") + ". Accessibility: " + if(RGL_ACCESS_CLEAR_WIDTH_MM<>"",RGL_ACCESS_CLEAR_WIDTH_MM+"mm clear","N/A") + ". Inspect interval: " + if(ASS_INSPECT_FREQ_TXT<>"",ASS_INSPECT_FREQ_TXT,"TBC") + ". Warranty: " + if(ASS_WARRANTY_TXT<>"",ASS_WARRANTY_TXT,"TBC") + "." | ASS_DESCRIPTION_TXT, PLM_PPE_MAT_TXT, PLM_PPE_SZ_MM, PLM_DRN_BODY_MAT_TXT, PLM_DRN_TRAP_TYPE_TXT, ASS_MANUFACTURER_TXT, ASS_MODEL_NR_TXT | PLM_HOTWTR_TEMP_C, PLM_HOTWTR_RECOVERY_L_H, PLM_PPE_FLW_LPS, PLM_PSR_KPA | RGL_NWSC_APPROVAL_TXT, RGL_ACCESS_CLEAR_WIDTH_MM, ASS_INSPECT_FREQ_TXT, ASS_WARRANTY_TXT | PLM_PPE_FLW_LPS > 0.15 (fixture) → [!FLOW] PLM_PSR_KPA out of range → [!PSR] | BOQ-PLM-SanitaryWC / BOQ-PLM-SanitaryWHB (sh.08) (sh.08) Bill No.5: WC/WHB/Urinal/Sink/Cleaner | BOQ-PLM-Sanitary | IMMEDIATE
Plumbing Equipment | PLM | PLM_TAG_7_PARA_EQUIPMENT_TXT | PLM_Eqp_Para.rfa | "This " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"plumbing equipment") + ", " + if(PLM_CAP_CU_M<>"",PLM_CAP_CU_M+"m³","?m³") + " capacity, " + if(PLM_PWR_KW<>"",PLM_PWR_KW+"kW","?kW") + ", " + if(PLM_HED_M<>"",PLM_HED_M+"m head","?m head") + ". By " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"TBC") + " model " + if(ASS_MODEL_NR_TXT<>"",ASS_MODEL_NR_TXT,"TBC") + "." | "Fuel: " + if(PLM_HOTWTR_FUEL_TXT<>"",PLM_HOTWTR_FUEL_TXT,"TBC") + ". Control: " + if(HVC_CONTROL_TYPE_TXT<>"",HVC_CONTROL_TYPE_TXT,"TBC") + ". Power: " + if(ELC_PNL_VLT_V<>"",ELC_PNL_VLT_V+"V","TBC") + "." | "NWSC approval: " + if(RGL_NWSC_APPROVAL_TXT<>"",RGL_NWSC_APPROVAL_TXT,"pending") + ". Inspect freq: " + if(ASS_INSPECT_FREQ_TXT<>"",ASS_INSPECT_FREQ_TXT,"TBC") + ". Warranty: " + if(ASS_WARRANTY_TXT<>"",ASS_WARRANTY_TXT,"TBC") + "." | ASS_DESCRIPTION_TXT, PLM_CAP_CU_M, PLM_PWR_KW, PLM_HED_M, ASS_MANUFACTURER_TXT, ASS_MODEL_NR_TXT | PLM_HOTWTR_FUEL_TXT, HVC_CONTROL_TYPE_TXT, ELC_PNL_VLT_V | RGL_NWSC_APPROVAL_TXT, ASS_INSPECT_FREQ_TXT, ASS_WARRANTY_TXT | PLM_PWR_KW, PLM_HED_M — no threshold | BOQ-PLM-WaterHeater (sh.08) (sh.08) Bill No.5: [DESC] [CAP]m³ pump/tank/heater | BOQ-PLM-Equipment | IMMEDIATE
Pipe Accessories | PLM | PLM_TAG_7_PARA_PIPEACC_TXT | PLM_Acc_Para.rfa | "This " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"pipe accessory") + ", " + if(PLM_VLV_BODY_MAT_TXT<>"",PLM_VLV_BODY_MAT_TXT,"") + " body, DN" + if(PLM_VLV_SZ_NR<>"",PLM_VLV_SZ_NR,"?") + ", Cv " + if(PLM_VLV_CV_NR<>"",PLM_VLV_CV_NR,"TBC") + ", PN" + if(PLM_PSR_KPA<>"",PLM_PSR_KPA,"?") + "bar." | "Type: " + if(PLM_VLV_TYPE_TXT<>"",PLM_VLV_TYPE_TXT,"TBC") + ". Actuator: " + if(PLM_VLV_ACTUATOR_TXT<>"",PLM_VLV_ACTUATOR_TXT,"manual") + ". End connection: " + if(PLM_VLV_END_CONN_TXT<>"",PLM_VLV_END_CONN_TXT,"TBC") + "." | "Standard: " + if(RGL_STD_TXT<>"",RGL_STD_TXT,"BS EN 806") + ". Cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"WRAS approved") + ". Service life: " + if(ASS_WARRANTY_TXT<>"",ASS_WARRANTY_TXT,"TBC") + ". Inspect interval: " + if(ASS_INSPECT_FREQ_TXT<>"",ASS_INSPECT_FREQ_TXT,"annual") + "." | ASS_DESCRIPTION_TXT, PLM_VLV_BODY_MAT_TXT, PLM_VLV_SZ_NR, PLM_VLV_CV_NR, PLM_PSR_KPA | PLM_VLV_TYPE_TXT, PLM_VLV_ACTUATOR_TXT, PLM_VLV_END_CONN_TXT | RGL_STD_TXT, ASS_QA_CERT_TXT, ASS_WARRANTY_TXT, ASS_INSPECT_FREQ_TXT | PLM_PSR_KPA out of range → [!PSR] | BOQ-PLM-Valves (sh.08) Bill No.5: [SZ]mm [TYPE] valve | BOQ-PLM-Valves | HIGH
MEP — FIRE LIFE SAFETY
Fire Alarm Devices | FLS | FLS_TAG_7_PARA_FA_TXT | FLS_FA_Para.rfa | if(FLS_SFTY_DEV_TYPE_TXT<>"",FLS_SFTY_DEV_TYPE_TXT,"Fire alarm device") + " point, " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","?mm") + " heavy gauge PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"") + " conduit complete with all accessories." | "Coverage: " + if(FLS_SFTY_COVERAGE_AREA_SQ_M<>"",FLS_SFTY_COVERAGE_AREA_SQ_M+"m²","TBC") + ". Zone: " + if(FLS_SFTY_ZONE_NR<>"",FLS_SFTY_ZONE_NR,"TBC") + ". Loop: " + if(FLS_SFTY_LOOP_NR<>"",FLS_SFTY_LOOP_NR,"TBC") + ". Panel: " + if(ELC_PNL_DESIGNATION_NAME_TXT<>"",ELC_PNL_DESIGNATION_NAME_TXT,"TBC") + "." | "Standard: BS 5839. Approval: " + if(RGL_KCCA_APPROVAL_TXT<>"",RGL_KCCA_APPROVAL_TXT,"pending") + ". Commissioning cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"TBC") + "." | FLS_SFTY_DEV_TYPE_TXT, ELC_CDT_SZ_MM, ELC_CDT_INSTALL_METHOD_TXT | FLS_SFTY_COVERAGE_AREA_SQ_M, FLS_SFTY_ZONE_NR, FLS_SFTY_LOOP_NR, ELC_PNL_DESIGNATION_NAME_TXT | RGL_KCCA_APPROVAL_TXT, ASS_QA_CERT_TXT | FLS_SFTY_COVERAGE_AREA_SQ_M > 21 → [!COVERAGE > 21m²] | BOQ-ELC-FireAlarm (sh.08) Bill No.4: FA points (detectors/MCP/sounders) | BOQ-ELC-FireAlarm | IMMEDIATE
Sprinklers | FLS | FLS_TAG_7_PARA_SPR_TXT | FLS_Spr_Para.rfa | "Sprinkler head " + if(FLS_SFTY_TEMP_RATING_C<>"",FLS_SFTY_TEMP_RATING_C+"°C","?°C") + " resistant. Flow: " + if(FLS_SFTY_FLW_RATE_LPM_NR<>"",FLS_SFTY_FLW_RATE_LPM_NR+"L/min","TBC") + ". Coverage: " + if(FLS_SFTY_COVERAGE_AREA_SQ_M<>"",FLS_SFTY_COVERAGE_AREA_SQ_M+"m²","TBC") + "." | "Type: " + if(FLS_SFTY_DEV_TYPE_TXT<>"",FLS_SFTY_DEV_TYPE_TXT,"TBC") + ". K-factor: " + if(FLS_SFTY_K_FACTOR_NR<>"",FLS_SFTY_K_FACTOR_NR,"TBC") + ". RTI: " + if(FLS_SFTY_RTI_TXT<>"",FLS_SFTY_RTI_TXT,"TBC") + ". Zone: " + if(FLS_SFTY_ZONE_NR<>"",FLS_SFTY_ZONE_NR,"TBC") + "." | "Standard: BS EN 12845 / NFPA 13. Hazard class: " + if(FLS_SFTY_HAZARD_CLASS_TXT<>"",FLS_SFTY_HAZARD_CLASS_TXT,"TBC") + ". Commissioning: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"TBC") + "." | FLS_SFTY_TEMP_RATING_C, FLS_SFTY_FLW_RATE_LPM_NR, FLS_SFTY_COVERAGE_AREA_SQ_M | FLS_SFTY_DEV_TYPE_TXT, FLS_SFTY_K_FACTOR_NR, FLS_SFTY_RTI_TXT, FLS_SFTY_ZONE_NR | FLS_SFTY_HAZARD_CLASS_TXT, ASS_QA_CERT_TXT | TEMP < 57 or > 79 → [!TEMP OUT OF RANGE] COVERAGE > 21 → [!COVERAGE > 21m²] | BOQ-FLS-Sprinklers (sh.08) (sh.08) Bill No.6: Sprinkler heads [TEMP]°C | BOQ-FLS-Sprinklers | IMMEDIATE
ICT, SECURITY & SPECIALTY
Communication Devices (BMS) | ELEC/ICT | COM_TAG_7_PARA_BMS_TXT | COM_Para.rfa | "This " + if(COM_C_DEV_TYPE_TXT<>"",COM_C_DEV_TYPE_TXT,"BMS device") + ", network " + if(COM_C_NETWORK_ADDRESS_TXT<>"",COM_C_NETWORK_ADDRESS_TXT,"TBC") + ", BACnet instance " + if(COM_C_DEV_BACNET_INSTANCE_INT<>"",COM_C_DEV_BACNET_INSTANCE_INT,"?") + ". Controller: " + if(COM_C_DEV_CONTROLLER_NAME_TXT<>"",COM_C_DEV_CONTROLLER_NAME_TXT,"TBC") + "." | "Protocol: " + if(COM_C_PROTOCOL_TXT<>"",COM_C_PROTOCOL_TXT,"BACnet/IP") + ". Range: " + if(COM_C_MEAS_RANGE_TXT<>"",COM_C_MEAS_RANGE_TXT,"TBC") + ". Power: " + if(ELC_PNL_VLT_V<>"",ELC_PNL_VLT_V+"V","TBC") + ". Cable: " + if(ELC_CBL_TYPE_TXT<>"",ELC_CBL_TYPE_TXT,"TBC") + "." | "BACnet cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"pending") + ". Controller map: " + if(ASS_INST_DETAIL_NUM_TXT<>"",ASS_INST_DETAIL_NUM_TXT,"TBC") + ". Inspect freq: " + if(ASS_INSPECT_FREQ_TXT<>"",ASS_INSPECT_FREQ_TXT,"TBC") + "." | COM_C_DEV_TYPE_TXT, COM_C_NETWORK_ADDRESS_TXT, COM_C_DEV_BACNET_INSTANCE_INT, COM_C_DEV_CONTROLLER_NAME_TXT | COM_C_PROTOCOL_TXT, COM_C_MEAS_RANGE_TXT, ELC_PNL_VLT_V, ELC_CBL_TYPE_TXT | ASS_QA_CERT_TXT, ASS_INST_DETAIL_NUM_TXT, ASS_INSPECT_FREQ_TXT | COM_C_DEV_BACNET_INSTANCE_INT duplicate → [!BACNET_ID CONFLICT] if(COM_C_MEAS_RANGE_TXT="","[!RANGE NOT SET]","") | BOQ-ICT-BMS (sh.08) Bill No.9: [TYPE] BMS controller | BOQ-ICT-BMS | HIGH
Data / Telephone Devices | ELEC/ICT | ICT_TAG_7_PARA_DATA_TXT | ICT_Para.rfa | if(ICT_OUTLET_TYPE_TXT<>"",ICT_OUTLET_TYPE_TXT,"Data") + " outlet, port " + if(ICT_PORT_NR<>"",ICT_PORT_NR,"?") + ", patch panel " + if(ICT_PATCH_PANEL_TXT<>"",ICT_PATCH_PANEL_TXT,"TBC") + ". Type: " + if(COM_C_DEV_TYPE_TXT<>"",COM_C_DEV_TYPE_TXT,"TBC") + "." | "Cable: " + if(ELC_CBL_SZ_MM2<>"",ELC_CBL_SZ_MM2+"mm² Cat","TBC Cat") + if(ICT_CAT_RATING_TXT<>"",ICT_CAT_RATING_TXT,"?") + ". Conduit: " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm PVC","TBC") + "." | "Tested to: TIA-568-C.2 Cat " + if(ICT_CAT_RATING_TXT<>"",ICT_CAT_RATING_TXT,"6") + ". Test cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"pending") + ". Standard: TIA/EIA-568." | ICT_OUTLET_TYPE_TXT, ICT_PORT_NR, ICT_PATCH_PANEL_TXT, COM_C_DEV_TYPE_TXT | ELC_CBL_SZ_MM2, ICT_CAT_RATING_TXT, ELC_CDT_SZ_MM | ICT_CAT_RATING_TXT, ASS_QA_CERT_TXT | ICT_CAT_RATING_TXT < 6 → [!CAT < 6] ELC_CDT_CBL_FILL_PCT > 40 → [!FILL > 40%] | BOQ-ICT-DataOutlets (sh.08) Bill No.9: Cat[X] data/telephone outlet | BOQ-ICT-DataOutlets | MEDIUM
Security Devices | ELEC/ICT | SEC_TAG_7_PARA_SECURITY_TXT | SEC_Para.rfa | if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"Security device") + " zone " + if(SEC_DEV_ZONE_TXT<>"",SEC_DEV_ZONE_TXT,"?") + ". Cable: " + if(SEC_CBL_NR<>"",SEC_CBL_NR,"TBC") + ". Type: " + if(COM_C_DEV_TYPE_TXT<>"",COM_C_DEV_TYPE_TXT,"TBC") + "." | "Connection: " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm PVC conduit","TBC") + ". Power: " + if(ELC_PNL_VLT_V<>"",ELC_PNL_VLT_V+"V","TBC") + "." | "Access policy: " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"TBC") + ". Cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"TBC") + "." | ASS_DESCRIPTION_TXT, SEC_DEV_ZONE_TXT, SEC_CBL_NR, COM_C_DEV_TYPE_TXT | ELC_CDT_SZ_MM, ELC_PNL_VLT_V | ASS_QA_CERT_TXT | ELC_VLT_DROP_PCT > 4.0 → [!VD > 4%] if(SEC_DEV_ZONE_TXT="","[!NO ZONE ASSIGNED]","") | BOQ-ELC-Security (sh.08) Bill No.4: CCTV/access control points | BOQ-ELC-Security | MEDIUM
Specialty Equipment (Lifts/Gen/ATS) | MULTI | ASS_TAG_7_PARA_EQUIPMENT_TXT | ASS_Eqp_Para.rfa | "This " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"specialty equipment") + " (" + if(ASS_SYSTEM_TYPE_TXT<>"",ASS_SYSTEM_TYPE_TXT,"system TBC") + "). By " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"TBC") + " model " + if(ASS_MODEL_NR_TXT<>"",ASS_MODEL_NR_TXT,"TBC") + ". Tag: " + if(ASS_EQUIPMENT_TAG_TXT<>"",ASS_EQUIPMENT_TAG_TXT,"TBC") + "." | "Capacity: " + if(ASS_CAPACITY_TXT<>"",ASS_CAPACITY_TXT,"TBC") + ". Power: " + if(HVC_PWR_KW<>"",HVC_PWR_KW+"kW","TBC") + ". Drive: " + if(ASS_DRIVE_TXT<>"",ASS_DRIVE_TXT,"TBC") + "." | "Commissioning cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"TBC") + ". Govt lift inspector cert (lifts): " + if(RGL_KCCA_APPROVAL_TXT<>"",RGL_KCCA_APPROVAL_TXT,"pending") + ". Warranty: " + if(ASS_WARRANTY_TXT<>"",ASS_WARRANTY_TXT,"TBC") + "." | ASS_DESCRIPTION_TXT, ASS_SYSTEM_TYPE_TXT, ASS_MANUFACTURER_TXT, ASS_MODEL_NR_TXT, ASS_EQUIPMENT_TAG_TXT | ASS_CAPACITY_TXT, HVC_PWR_KW, ASS_DRIVE_TXT | ASS_QA_CERT_TXT, RGL_KCCA_APPROVAL_TXT, ASS_WARRANTY_TXT | HVC_PWR_KW > rated_KW*1.05 → [!OVERPOWER] RGL_KCCA_APPROVAL_TXT absent (lifts) → [!NO KCCA APPROVAL] | BOQ-LIFT-Equipment (sh.08) (sh.08) Bill No.8: [DESC] lift [CAP]kg [STOPS]stops | BOQ-LIFT-Equipment | MEDIUM
Nurse Call Devices | ELEC/ICT | NCL_TAG_7_PARA_NURSECALL_TXT | NCL_Para.rfa | if(NCL_CALL_TYPE_TXT<>"",NCL_CALL_TYPE_TXT,"Nurse call") + " device, zone " + if(NCL_ZONE_TXT<>"",NCL_ZONE_TXT,"?") + ". Type: " + if(COM_C_DEV_TYPE_TXT<>"",COM_C_DEV_TYPE_TXT,"TBC") + "." | "Protocol: " + if(COM_C_PROTOCOL_TXT<>"",COM_C_PROTOCOL_TXT,"TBC") + ". Cable: " + if(ELC_CBL_TYPE_TXT<>"",ELC_CBL_TYPE_TXT,"TBC") + "." | "Standard: HTM 08-03. Zone test: " + if(NCL_ZONE_TXT<>"",NCL_ZONE_TXT,"TBC") + ". Cert: " + if(ASS_QA_CERT_TXT<>"",ASS_QA_CERT_TXT,"pending") + ". Response time standard: 3 min." | NCL_CALL_TYPE_TXT, NCL_ZONE_TXT, COM_C_DEV_TYPE_TXT | COM_C_PROTOCOL_TXT, ELC_CBL_TYPE_TXT | NCL_ZONE_TXT, ASS_QA_CERT_TXT | if(NCL_ZONE_TXT="","[!NO ZONE]","") + if(COM_C_PROTOCOL_TXT="","[!NO PROTOCOL]","") | BOQ-ICT-NurseCall (sh.08) (sh.08) Bill No.9: Nurse call points (healthcare) | BOQ-ICT-NurseCall | PROJECT

## 08-BOQ-TEMPLATE-SCHEDULES
BOQ TEMPLATE SCHEDULES v4.3 ¦ Uganda PPDA Structure ¦ 9 Bills ¦ Revit schedule definitions for automated BOQ export
USAGE: Each named schedule (Column H) is a Revit Schedule/Quantities view. Calculated value in "BOQ_DESC" field assembles the item description from parameter tokens (Column K). Export schedule to Excel → paste Unit/Qty columns into priced BOQ template. Rate and Amount columns are filled by QS.
Item | Description (BOQ item — assembled from Revit params) | Unit | Qty | Rate (UGX) | Amount (UGX) | Revit Category | Revit Schedule Name | Qty Source | Calculated Value Formula (Edit Label / Schedule) | Parameter Tokens used | BOQ Map ref (sh.04) | Warning params | Notes / Uganda-specific
BILL No.1 — PRELIMINARIES
1.1 Contractor Obligations & Project Setup
1.1.1 | Allow for temporary water supply for construction purposes including piping from source to works and all necessary connections | Item | [5 empty] | Manual entry | N/A — manual item | N/A | Bill1-Prelim |  | Uganda: NWSC connection required. Allow plumber fees.
1.1.2 | Allow for providing and maintaining a weatherproof lockable store for materials and plant for the duration of the contract | Item | [5 empty] | Manual entry | N/A | N/A | Bill1-Prelim
1.1.3 | Allow for temporary electrical power supply including generator, wiring, and distribution for the duration of the contract | Item | [5 empty] | Manual entry | N/A | N/A | Bill1-Prelim |  | Uganda: UMEME connection or diesel gen.
1.1.4 | Allow for provision of security to protect the works and materials for the duration of the contract | Item | [5 empty] | Manual entry | N/A | N/A | Bill1-Prelim
1.1.5 | Allow for setting out the works including survey equipment and all associated costs | Item | [5 empty] | Manual entry | N/A | N/A | Bill1-Prelim
1.1.6 | Allow for insurance of the works, public liability insurance, and workmen's compensation for the duration of the contract | Item | [5 empty] | Manual entry | N/A | N/A | Bill1-Prelim |  | PPDA requires evidence of insurance.
1.1.7 | Allow for all health and safety requirements including personal protective equipment, first aid, and site signage | Item | [5 empty] | Manual entry | N/A | N/A | Bill1-Prelim |  | Uganda OSH Act compliance.
1.1.8 | Allow for demobilisation, clearing site, and removal of all temporary works on completion | Item | [5 empty] | Manual entry | N/A | N/A | Bill1-Prelim
BILL No.2 — TOOLS & EQUIPMENT
2.1 Plant & Tools for Construction Use
2.1.1 | Provide wheelbarrows of approved design for the duration of the works | No. | [5 empty] | Manual | N/A | N/A | Bill2-Tools |  | Standard PPDA prelim item.
2.1.2 | Provide spades, shovels, hoes, and hand tools for the duration of the works | Set | [5 empty] | Manual | N/A | N/A | Bill2-Tools
2.1.3 | Provide concrete mixer (0.5 bag) for the duration of the works | No. | [5 empty] | Manual | N/A | N/A | Bill2-Tools
2.1.4 | Provide pulley / chain block hoist (1 tonne minimum) for the duration of the works | No. | [5 empty] | Manual | N/A | N/A | Bill2-Tools |  | Required for MEP equipment lifts.
2.1.5 | Provide scaffolding and access equipment for all works above 2m height for the duration of the works | m² | [5 empty] | Manual | N/A | N/A | Bill2-Tools
2.1.6 | Provide vibrator for concrete compaction for the duration of the works | No. | [5 empty] | Manual | N/A | N/A | Bill2-Tools
BILL No.3 — ARCHITECTURAL / STRUCTURAL WORKS
3.1 SUBSTRUCTURE
3.1.1 | Excavation in soft / medium ground for foundations as shown on drawings to required depth | m³ |  |  |  | Structural Foundations | BOQ-STR-Foundations | Rooms/Spaces model volume or manual | "Excavation: " + if(BLE_ROOM_VOLUME_M3<>"",BLE_ROOM_VOLUME_M3+"m³","TBC") | BLE_ROOM_VOLUME_M3 | Bill3-Excavation |  | Soil classification by geotech report.
3.1.2 | [GRADE] concrete grade strip / pad / raft foundations [THICKNESS]mm thick as structural drawings. Reinf. per BBS. | m³ |  |  |  | Structural Foundations | BOQ-STR-Foundations | Structural Foundations count/volume | "Grade " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"C25") + " concrete foundations " + if(BLE_STRUCT_THICKNESS_MM<>"",BLE_STRUCT_THICKNESS_MM+"mm thick","as drawings") + " reinforced per BBS." | BLE_STRUCT_CONCRETE_GRADE_TXT, BLE_STRUCT_THICKNESS_MM | BOQ-STR-Foundations | BLE_STRUCT_CONCRETE_GRADE_TXT | BOQ-ARCH-Foundations schedule. Qty=volume from model.
3.1.3 | Blinding concrete [GRADE], [THICKNESS]mm thick below foundations | m³ |  |  |  | Structural Foundations | BOQ-STR-Foundations | Area x thickness | "Grade " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"C15") + " blinding " + if(BLE_STRUCT_THICKNESS_MM<>"",BLE_STRUCT_THICKNESS_MM+"mm","75mm") + " thick." | BLE_STRUCT_CONCRETE_GRADE_TXT, BLE_STRUCT_THICKNESS_MM | BOQ-STR-Blinding
3.1.4 | [SZ]mm dia. reinforcement bars [GRADE] to foundations, columns, and ground beams as BBS | Ton |  |  |  | Structural Foundations | BOQ-STR-Foundations | Rebar schedule / manual | "Y" + if(BLE_STRUCT_REBAR_DIA_MM<>"",BLE_STRUCT_REBAR_DIA_MM,"TBC") + " Grade " + if(BLE_STRUCT_STEEL_GRADE_TXT<>"",BLE_STRUCT_STEEL_GRADE_TXT,"Fe500") + " reinforcement bars to foundations." | BLE_STRUCT_REBAR_DIA_MM, BLE_STRUCT_STEEL_GRADE_TXT | BOQ-STR-Rebar
3.1.5 | [THICKNESS]mm thick [GRADE] reinforced concrete slab on grade with [MESH] BRC mesh, surface power-floated | m² |  |  |  | Structural Foundations | BOQ-STR-Foundations | Floor area from model | "Grade " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"C25") + " slab " + if(BLE_STRUCT_THICKNESS_MM<>"",BLE_STRUCT_THICKNESS_MM+"mm thick","TBC thick") + " with BRC mesh, power-floated." | BLE_STRUCT_CONCRETE_GRADE_TXT, BLE_STRUCT_THICKNESS_MM | BOQ-STR-Slab
3.1.6 | [DEPTH]mm thick hardcore filling well consolidated in layers not exceeding 150mm, blinded with 50mm sand | m³ |  |  |  | Structural Foundations | BOQ-STR-Foundations | Volume from model | "Hardcore fill " + if(BLE_STRUCT_THICKNESS_MM<>"",BLE_STRUCT_THICKNESS_MM+"mm deep","as drawings") + " consolidated in 150mm layers, blinded 50mm sand." | BLE_STRUCT_THICKNESS_MM | BOQ-STR-Hardcore
3.1.7 | Damp proof membrane 1000 gauge polythene sheet with 150mm laps welded and turned up walls | m² |  |  |  | Structural Foundations | BOQ-STR-Foundations | Floor area | "1000g polythene DPM lapped 150mm and turned up walls." | N/A | BOQ-STR-DPM
3.2 WALLING
3.2.1 | [THICKNESS]mm thick [TYPE] [MATERIAL] walling as drawings — [FUNCTION] wall | m² |  |  |  | Walls | BOQ-ARCH-Walling | Walls schedule — Area param | "if(BLE_WALL_THICKNESS_MM<>"",BLE_WALL_THICKNESS_MM+"mm ","") + if(BLE_WALL_TYPE_CLASSIFICATION_TXT<>"",BLE_WALL_TYPE_CLASSIFICATION_TXT+" ","") + if(BLE_WALL_PRIMARY_WALL_MAT_TXT<>"",BLE_WALL_PRIMARY_WALL_MAT_TXT+" walling ","walling ") + if(BLE_WALL_FUNCTION_TXT<>"","("+BLE_WALL_FUNCTION_TXT+")","") + "." | BLE_WALL_THICKNESS_MM, BLE_WALL_TYPE_CLASSIFICATION_TXT, BLE_WALL_PRIMARY_WALL_MAT_TXT, BLE_WALL_FUNCTION_TXT | BOQ-ARCH-Walling | PER_THERM_U_VALUE_W_M2K_NR > 0.70 → [!U > 0.70] | BOQ-ARCH-Walling schedule. Group by type mark. U-value warning for external walls.
3.2.2 | [THICKNESS]mm thick internal partition walls [MATERIAL] as room data sheets | m² |  |  |  | Walls | BOQ-ARCH-Walling | Walls schedule — internal filter | "if(BLE_WALL_THICKNESS_MM<>"",BLE_WALL_THICKNESS_MM+"mm ","") + if(BLE_WALL_PRIMARY_WALL_MAT_TXT<>"",BLE_WALL_PRIMARY_WALL_MAT_TXT+" ","") + "internal partition wall." | BLE_WALL_THICKNESS_MM, BLE_WALL_PRIMARY_WALL_MAT_TXT | BOQ-ARCH-Partitions
3.2.3 | External [MATERIAL] plaster/render finish [THICKNESS]mm thick to all external faces of walling | m² |  |  |  | Walls | BOQ-ARCH-Walling | Wall face area (exterior finish) | "if(BLE_WALL_EXTERIOR_FINISH_TXT<>"",BLE_WALL_EXTERIOR_FINISH_TXT+" finish ","External plaster ") + "to all external faces." | BLE_WALL_EXTERIOR_FINISH_TXT | BOQ-ARCH-ExternalPlaster
3.2.4 | Internal plaster/skim coat [MATERIAL] finish to all internal faces of walling | m² |  |  |  | Walls | BOQ-ARCH-Walling | Wall face area (interior finish) | "if(BLE_WALL_INTERIOR_FINISH_TXT<>"",BLE_WALL_INTERIOR_FINISH_TXT+" finish ","Internal plaster ") + "to all internal faces." | BLE_WALL_INTERIOR_FINISH_TXT | BOQ-ARCH-InternalPlaster
3.2.5 | [COLOUR] paint [TYPE] two coats on internal plastered walls | m² |  |  |  | Walls | BOQ-ARCH-InternalPlaster | BOQ-ARCH-Paint — Area | "if(BLE_WALL_INTERIOR_FINISH_TXT<>\"\",BLE_WALL_INTERIOR_FINISH_TXT,\"[COLOUR]\")" + " paint two coats on internal plastered walls." | BLE_WALL_INTERIOR_FINISH_TXT | BOQ-ARCH-Paint
3.3 STRUCTURAL FRAME
3.3.1 | [GRADE] reinforced concrete columns [SZ]mm x [SZ]mm or [DIA]mm dia. as structural drawings | m³ |  |  |  | Structural Framing | BOQ-STR-Framing | Structural Columns schedule — volume | "Grade " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"C30") + " RC columns " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"as drawings") + ", reinforced per BBS." | BLE_STRUCT_CONCRETE_GRADE_TXT, ASS_DESCRIPTION_TXT | BOQ-STR-Columns | BLE_STRUCT_CONCRETE_GRADE_TXT | Group by column mark.
3.3.2 | [GRADE] reinforced concrete ground / suspended beams [SZ]mm wide x [DEPTH]mm deep as structural drawings | m³ |  |  |  | Structural Framing | BOQ-STR-Framing | Structural Framing schedule — volume | "Grade " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"C30") + " RC beam " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"as drawings") + " reinforced per BBS." | BLE_STRUCT_CONCRETE_GRADE_TXT, ASS_DESCRIPTION_TXT | BOQ-STR-Beams
3.3.3 | [GRADE] reinforced concrete suspended floor/roof slab [THICKNESS]mm thick including formwork | m² |  |  |  | Structural Framing | BOQ-STR-Framing | Floors schedule — area | "Grade " + if(BLE_STRUCT_CONCRETE_GRADE_TXT<>"",BLE_STRUCT_CONCRETE_GRADE_TXT,"C30") + " suspended slab " + if(BLE_STRUCT_THICKNESS_MM<>"",BLE_STRUCT_THICKNESS_MM+"mm thick,","as drawings,") + " including formwork." | BLE_STRUCT_CONCRETE_GRADE_TXT, BLE_STRUCT_THICKNESS_MM | BOQ-STR-Slab
3.3.4 | [GRADE] [SECTION] structural steel columns/frames/trusses including connections, bolts, and protective paint as structural drawings | Ton |  |  |  | Structural Framing | BOQ-STR-Framing | Structural Framing — manual or weight param | "Grade " + if(BLE_STRUCT_STEEL_GRADE_TXT<>"",BLE_STRUCT_STEEL_GRADE_TXT,"S275") + " structural steel " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"sections as drawings") + " with connections." | BLE_STRUCT_STEEL_GRADE_TXT, ASS_DESCRIPTION_TXT | BOQ-STR-SteelFrame |  | Used where steel frame specified.
3.4 ROOFING
3.4.1 | [TYPE] roofing sheet [MATERIAL] [GAUGE] fixed to [PURLINS] purlin structure including all accessories | m² |  |  |  | Roofs | BOQ-ARCH-Roofing | Roofs schedule — area | "if(BLE_ROOF_TYPE_TXT<>"",BLE_ROOF_TYPE_TXT+" ","") + if(BLE_ROOF_MATERIAL_TXT<>"",BLE_ROOF_MATERIAL_TXT+" roofing ","roofing ") + "to " + if(BLE_ROOF_PITCH_DEG<>"",BLE_ROOF_PITCH_DEG+"° pitch.","as drawings.") | BLE_ROOF_TYPE_TXT, BLE_ROOF_MATERIAL_TXT, BLE_ROOF_PITCH_DEG | BOQ-ARCH-Roofing | PER_THERM_U_VALUE_W_M2K_NR > 0.50 → [!U > 0.50] | Roof U-value most critical element in Uganda climate.
3.4.2 | Gutters [MATERIAL] [SIZE]mm including all brackets, joints, stopends and outlets | LM |  |  |  | Roofs | BOQ-ARCH-Roofing | Roof edge length / manual | "if(BLE_ROOF_GUTTER_MAT_TXT<>"",BLE_ROOF_GUTTER_MAT_TXT+" ","uPVC ") + "gutters " + if(BLE_ROOF_GUTTER_SZ_MM<>"",BLE_ROOF_GUTTER_SZ_MM+"mm,","as drawings,") + " with brackets, joints, and outlets." | BLE_ROOF_GUTTER_MAT_TXT, BLE_ROOF_GUTTER_SZ_MM | BOQ-ARCH-Gutters
3.4.3 | [MATERIAL] [DIA]mm diameter rainwater downpipes with all fixings and offsets | LM |  |  |  | Roofs | BOQ-ARCH-Roofing | Pipe length / manual | "if(PLM_PPE_MAT_TXT<>"",PLM_PPE_MAT_TXT+" ","uPVC ") + "rainwater downpipe " + if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm dia.","100mm dia.") + " with fixings." | PLM_PPE_MAT_TXT, PLM_PPE_SZ_MM | BOQ-PLM-RWP
3.4.4 | Thermal insulation to roof [MATERIAL] [THICKNESS]mm thick with vapour barrier where shown on drawings | m² |  |  |  | Roofs | BOQ-ARCH-Roofing | Roof area | "if(BLE_ROOF_INS_MAT_TXT<>"",BLE_ROOF_INS_MAT_TXT+" insulation ","Thermal insulation ") + if(BLE_ROOF_INS_THK_MM<>"",BLE_ROOF_INS_THK_MM+"mm thick.","as drawings.") | BLE_ROOF_INS_MAT_TXT, BLE_ROOF_INS_THK_MM | BOQ-ARCH-RoofIns
3.5 WINDOWS & DOORS
3.5.1 | [TYPE] window [W]mm wide x [H]mm high, [GLAZING] glazed, [FRAME] frame, [FINISH] finish, including all ironmongery, mosquito screen, and burglar bar as schedule | No. |  |  |  | Doors/Windows | BOQ-ARCH-Doors | Windows schedule — count by type | "if(BLE_WINDOW_OPERATION_TYPE_TXT<>"",BLE_WINDOW_OPERATION_TYPE_TXT+" ","") + "window " + if(BLE_WINDOW_WIDTH_MM<>"",BLE_WINDOW_WIDTH_MM+"W","?W") + "x" + if(BLE_WINDOW_HEIGHT_MM<>"",BLE_WINDOW_HEIGHT_MM+"H mm","?H mm") + ", " + if(BLE_WINDOW_GLAZING_TYPE_TXT<>"",BLE_WINDOW_GLAZING_TYPE_TXT+" glazed,","glazed,") + " frame: " + if(BLE_WINDOW_FRAME_MAT_TXT<>"",BLE_WINDOW_FRAME_MAT_TXT+",","TBC,") + " including ironmongery, mosquito screen, burglar bar." | BLE_WINDOW_OPERATION_TYPE_TXT, BLE_WINDOW_WIDTH_MM, BLE_WINDOW_HEIGHT_MM, BLE_WINDOW_GLAZING_TYPE_TXT, BLE_WINDOW_FRAME_MAT_TXT | BOQ-ARCH-Windows | BLE_WINDOW_U_VALUE_W_M_2K_NR > 3.00 → [!U > 3.00] BLE_WINDOW_SOLAR_HEAT_GAIN_COEFFICIENT_NR > 0.40 → [!SHGC > 0.40] | Group by window type mark. Uganda: mosquito screen and burglar bar standard.
3.5.2 | [TYPE] door [W]mm wide x [H]mm high, [MATERIAL] [FINISH], [FRAME] frame, complete with all ironmongery as door schedule | No. |  |  |  | Doors/Windows | BOQ-ARCH-Doors | Doors schedule — count by type | "if(BLE_DOOR_OPERATION_TYPE_TXT<>"",BLE_DOOR_OPERATION_TYPE_TXT+" ","") + "door " + if(BLE_DOOR_WIDTH_MM<>"",BLE_DOOR_WIDTH_MM+"W","?W") + "x" + if(BLE_DOOR_HEIGHT_MM<>"",BLE_DOOR_HEIGHT_MM+"H mm","?H mm") + ", " + if(BLE_DOOR_PRIMARY_MAT_TXT<>"",BLE_DOOR_PRIMARY_MAT_TXT+",","TBC,") + " complete with ironmongery." | BLE_DOOR_OPERATION_TYPE_TXT, BLE_DOOR_WIDTH_MM, BLE_DOOR_HEIGHT_MM, BLE_DOOR_PRIMARY_MAT_TXT | BOQ-ARCH-Doors | FLS_PROT_FLS_RESISTANCE_RATING_MINUTES_MIN < 30 → [!FRR < 30] (fire doors) | Group by door type mark. Fire doors flagged.
3.6 CEILINGS & FLOOR FINISHES
3.6.1 | [MATERIAL] [TYPE] suspended ceiling system [MODULE]mm x [MODULE]mm modules at [HEIGHT]mm FFL as room data sheets | m² |  |  |  | Ceilings/Floors | BOQ-ARCH-Ceilings | Ceilings schedule — area | "if(BLE_CEIL_MATERIAL_TXT<>"",BLE_CEIL_MATERIAL_TXT+" ","") + "suspended ceiling " + if(BLE_CEIL_TYPE_TXT<>"",BLE_CEIL_TYPE_TXT+" ","") + if(BLE_CEIL_MODULE_MM<>"",BLE_CEIL_MODULE_MM+"mm module ","") + "at " + if(BLE_CEIL_HEIGHT_MM<>"",BLE_CEIL_HEIGHT_MM+"mm FFL.","FFL as drawings.") | BLE_CEIL_MATERIAL_TXT, BLE_CEIL_TYPE_TXT, BLE_CEIL_MODULE_MM, BLE_CEIL_HEIGHT_MM | BOQ-ARCH-Ceilings | PER_ACOUSTICS_BACKGROUND_NOISE_DB > 40 → [!NOISE]
3.6.2 | [MATERIAL] [TYPE] floor tiling [SIZE]mm x [SIZE]mm with [GROUT] grout, laid to falls where required | m² |  |  |  | Ceilings/Floors | BOQ-ARCH-Ceilings | Floors schedule — area | "if(BLE_FLR_MATERIAL_TXT<>"",BLE_FLR_MATERIAL_TXT+" ","") + if(BLE_FLR_TYPE_TXT<>"",BLE_FLR_TYPE_TXT+" ","") + "floor " + if(BLE_FLR_TILE_SZ_MM<>"",BLE_FLR_TILE_SZ_MM+"mm tile ","tiles") + "laid to falls where required." | BLE_FLR_MATERIAL_TXT, BLE_FLR_TYPE_TXT, BLE_FLR_TILE_SZ_MM | BOQ-ARCH-FloorFinishes
3.6.3 | [MATERIAL] skirting [HEIGHT]mm high to all rooms as specified | LM |  |  |  | Ceilings/Floors | BOQ-ARCH-Ceilings | Perimeter of rooms | "if(BLE_FLR_SKIRTING_MAT_TXT<>"",BLE_FLR_SKIRTING_MAT_TXT+" ","") + "skirting " + if(BLE_FLR_SKIRTING_HGT_MM<>"",BLE_FLR_SKIRTING_HGT_MM+"mm high.","as specified.") | BLE_FLR_SKIRTING_MAT_TXT, BLE_FLR_SKIRTING_HGT_MM | BOQ-ARCH-Skirting
3.7 STAIRS, RAMPS & SPECIALIST ARCH
3.7.1 | [MATERIAL] stairs [RISE]mm rise x [GOING]mm going x [WIDTH]mm wide, [TREAD] tread finish, [HANDRAIL] handrail — [NR] risers | Flight |  |  |  | Stairs/Ramps | BOQ-ARCH-Stairs | Stairs schedule — count | "if(BLE_STAIR_MAT_TXT<>"",BLE_STAIR_MAT_TXT+" ","") + "stair " + if(BLE_STAIR_RISE_MM<>"",BLE_STAIR_RISE_MM+"R/","?R/") + if(BLE_STAIR_GOING_MM<>"",BLE_STAIR_GOING_MM+"G mm, ","?G mm, ") + if(BLE_STAIR_WIDTH_MM<>"",BLE_STAIR_WIDTH_MM+"mm wide, ","?mm wide, ") + if(BLE_STAIR_TREAD_FINISH_TXT<>"",BLE_STAIR_TREAD_FINISH_TXT+" tread, ","") + if(BLE_STAIR_HANDRAIL_MAT_TXT<>"",BLE_STAIR_HANDRAIL_MAT_TXT+" handrail.","handrail.") | BLE_STAIR_MAT_TXT, BLE_STAIR_RISE_MM, BLE_STAIR_GOING_MM, BLE_STAIR_WIDTH_MM, BLE_STAIR_TREAD_FINISH_TXT, BLE_STAIR_HANDRAIL_MAT_TXT | BOQ-ARCH-Stairs | BLE_STAIR_RISE_MM > 190 → [!RISE] BLE_STAIR_WIDTH_MM < 1000 → [!WIDTH] | Uganda PWD requirements: min 1200mm width for public stairs.
3.7.2 | [MATERIAL] access ramp at [SLOPE]% gradient, [SURFACE] surface finish, [HANDRAIL] handrails both sides, [WIDTH]mm clear width | LM |  |  |  | Stairs/Ramps | BOQ-ARCH-Stairs | Ramps schedule — length | "if(BLE_RAMP_SLOPE_PCT<>"",BLE_RAMP_SLOPE_PCT+"% gradient ","") + "ramp, " + if(BLE_RAMP_SURFACE_FINISH_TXT<>"",BLE_RAMP_SURFACE_FINISH_TXT+" surface,","") + " handrails both sides, " + if(RGL_ACCESS_CLEAR_WIDTH_MM<>"",RGL_ACCESS_CLEAR_WIDTH_MM+"mm clear width.","as drawings.") | BLE_RAMP_SLOPE_PCT, BLE_RAMP_SURFACE_FINISH_TXT, RGL_ACCESS_CLEAR_WIDTH_MM | BOQ-ARCH-Ramps | BLE_RAMP_SLOPE_PCT > 8.33 → [!SLOPE] RGL_ACCESS_CLEAR_WIDTH_MM < 900 → [!WIDTH] | Uganda PWD Act 2020: max 1:12 gradient.
BILL No.4 — ELECTRICAL INSTALLATIONS
Preamble: Provide all materials, install, connect and set to work the following all as described in the Specifications and Drawings. All wiring by copper conductors to IEC 60227/60245. Conduits: PVC heavy gauge to BS 6053. Switchgear: IEC 60947. UMEME commissioning approval required.
4.1 WIRING CIRCUITS & CONDUITS
4.1.1 | Lighting points wired by [CBL_TYPE] copper cables in [CDT_SZ]mm heavy gauge PVC [METHOD] conduit with drops concealed in walls to switch positions complete with [MFR] steel boxes and all accessories. | No. |  |  |  | Electrical Fixtures/Conduits | BOQ-ELC-Lighting-Points | BOQ-ELC-Lighting-Points schedule — Count | "Lighting points wired by " + if(ELC_CKT_CBL_TYPE_TXT<>"",ELC_CKT_CBL_TYPE_TXT,"3x1.5mm² SC PVC") + " copper cables in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " heavy gauge PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"concealed") + " conduit with drops concealed in walls complete with " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"MK") + " steel boxes and all accessories." | ELC_CKT_CBL_TYPE_TXT, ELC_CDT_SZ_MM, ELC_CDT_INSTALL_METHOD_TXT, ASS_MANUFACTURER_TXT | BOQ-ELC-Lighting-Points | ELC_VLT_DROP_PCT > 4.0 → [!VD > 4%] | Group by floor. Per Uganda police CDAC BOQ format.
4.1.2 | Socket outlet points wired as a ring/radial by [CBL_TYPE] copper cables in [CDT_SZ]mm heavy gauge PVC [METHOD] conduit/trunking complete with boxes for sockets and all accessories. | No. |  |  |  | Electrical Fixtures/Conduits | BOQ-ELC-Lighting-Points | BOQ-ELC-Socket-Points — Count | "Socket outlet points wired as a ring by " + if(ELC_CKT_CBL_TYPE_TXT<>"",ELC_CKT_CBL_TYPE_TXT,"3x2.5mm² SC PVC") + " copper cables in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " heavy gauge PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"concealed") + " conduit/trunking complete with boxes and all accessories." | ELC_CKT_CBL_TYPE_TXT, ELC_CDT_SZ_MM, ELC_CDT_INSTALL_METHOD_TXT | BOQ-ELC-Socket-Points | ELC_VLT_DROP_PCT > 4.0 → [!VD > 4%]
4.1.3 | [CDT_SZ]mm heavy gauge PVC [METHOD] conduit complete with all accessories (for spare containment) | LM |  |  |  | Electrical Fixtures/Conduits | BOQ-ELC-Lighting-Points | BOQ-ELC-Conduits — Length | "if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " heavy gauge PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"concealed") + " conduit complete with all accessories." | ELC_CDT_SZ_MM, ELC_CDT_MAT_TXT, ELC_CDT_INSTALL_METHOD_TXT | BOQ-ELC-Conduits | ELC_CDT_CBL_FILL_PCT > 40 → [!FILL > 40%] | Group by size and installation method.
4.1.4 | Steel cable tray [WIDTH]mm x [DEPTH]mm fixed in cable duct or on wall brackets complete with all fittings and accessories | LM |  |  |  | Electrical Fixtures/Conduits | BOQ-ELC-Lighting-Points | BOQ-ELC-CableTrays — Length | "Steel cable tray " + if(ELC_CTR_WIDTH_MM<>"",ELC_CTR_WIDTH_MM,"100") + "x" + if(ELC_CTR_DEPTH_MM<>"",ELC_CTR_DEPTH_MM,"50") + "mm complete with all fittings and accessories." | ELC_CTR_WIDTH_MM, ELC_CTR_DEPTH_MM, ELC_CTR_MAT_TXT | BOQ-ELC-CableTrays | ELC_CTR_FILL_PCT > 45 → [!FILL > 45%] | Group by size.
4.2 LUMINAIRES & ACCESSORIES
4.2.1 | [TYPE] [WATT]W LED luminaire [MOUNTING], [SIZE]mm, with [CTRL] interface as [MFR] or equal approved. (Light Type [CODE]) | No. |  |  |  | Lighting Fixtures | BOQ-ELC-Luminaires | BOQ-ELC-Luminaires — Count | "if(LTG_FIX_TYPE_CLASSIFICATION_TXT<>"",LTG_FIX_TYPE_CLASSIFICATION_TXT+" ","") + if(LTG_FIX_LMP_WATTAGE_W<>"",LTG_FIX_LMP_WATTAGE_W+"W ","") + "LED luminaire, " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"as spec,") + " as " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"approved manufacturer") + " or equal approved." | LTG_FIX_TYPE_CLASSIFICATION_TXT, LTG_FIX_LMP_WATTAGE_W, ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT | BOQ-ELC-Luminaires | LTG_EFFICACY_LM_W < 80 → [!EFFICACY] | Group by type mark.
4.2.2 | [RATING]A [GANGS] gang [WAYS] way light switch [MFR] or equal approved complete with all accessories | No. |  |  |  | Lighting Fixtures | BOQ-ELC-Luminaires | BOQ-ELC-Switches — Count | "if(ELC_CKT_BRK_RATING_A<>"",ELC_CKT_BRK_RATING_A+"A ","10A ") + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"1 gang 1 way ") + "light switch as " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"MK or Schneider") + " or equal approved, complete with all accessories." | ELC_CKT_BRK_RATING_A, ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT | BOQ-ELC-Switches
4.2.3 | [RATING]A [POLES]pin [CONFIG] switched socket outlets on wall/trunking as [MFR] or equal approved | No. |  |  |  | Lighting Fixtures | BOQ-ELC-Luminaires | BOQ-ELC-Sockets — Count | "if(ELC_CKT_BRK_RATING_A<>"",ELC_CKT_BRK_RATING_A+"A ","13A ") + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"3-pin double ") + "switched socket outlet, " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"MK or equal") + " or equal approved." | ELC_CKT_BRK_RATING_A, ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT | BOQ-ELC-Sockets
4.3 DISTRIBUTION BOARDS & SWITCHGEAR
4.3.1 | [DESIGNATION] distribution board, [VLT]V [PHS]-phase, [WAYS] ways, [MAIN]A main breaker, [SC]kA fault rating, IP[IP] enclosure, complete with all MCBs, RCDs, bus bars and accessories as single line diagram | No. |  |  |  | Electrical Equipment | BOQ-ELC-DBPanels | BOQ-ELC-DBPanels — Count | "if(ELC_PNL_DESIGNATION_NAME_TXT<>"",ELC_PNL_DESIGNATION_NAME_TXT,"DB") + " distribution board, " + if(ELC_PNL_VLT_V<>"",ELC_PNL_VLT_V+"V ","230V ") + if(ELC_PNL_PHS_COUNT_NR<>"",ELC_PNL_PHS_COUNT_NR+"-phase, ","1-phase, ") + if(ELC_PNL_NUM_OF_WAYS_NR<>"",ELC_PNL_NUM_OF_WAYS_NR+" ways, ","? ways, ") + if(ELC_PNL_MAIN_BRK_A<>"",ELC_PNL_MAIN_BRK_A+"A main, ","?A main, ") + if(ELC_PNL_SHORT_CIRCUIT_KA<>"",ELC_PNL_SHORT_CIRCUIT_KA+"kA fault, ","?kA, ") + "complete with all MCBs, RCDs and accessories." | ELC_PNL_DESIGNATION_NAME_TXT, ELC_PNL_VLT_V, ELC_PNL_PHS_COUNT_NR, ELC_PNL_NUM_OF_WAYS_NR, ELC_PNL_MAIN_BRK_A, ELC_PNL_SHORT_CIRCUIT_KA | BOQ-ELC-DBPanels | ELC_PNL_CONNECTED_LOAD_KW > ELC_PNL_RATED_KW*0.8 → [!OVERLOADED] ELC_PNL_SHORT_CIRCUIT_KA < 6 → [!SC < 6kA] | 1 schedule row per panel. UMEME approval required.
4.3.2 | Main [VLT]V [PHASES]-phase incoming supply cable [SIZE]mm² [TYPE] from UMEME metering point to main distribution board complete with all accessories | LM |  |  |  | Electrical Equipment | BOQ-ELC-DBPanels | Manual / cable schedule | "if(ELC_CBL_SZ_MM2<>"",ELC_CBL_SZ_MM2+"mm² ","?mm² ") + if(ELC_CKT_CBL_TYPE_TXT<>"",ELC_CKT_CBL_TYPE_TXT,"SWA XLPE") + " main incoming cable from UMEME metering to MDB." | ELC_CBL_SZ_MM2, ELC_CKT_CBL_TYPE_TXT | BOQ-ELC-IncomingCable
4.4 FIRE ALARM & SECURITY SYSTEMS
4.4.1 | Fire alarm [TYPE] points (detectors/MCPs/sounders) in [CDT_SZ]mm heavy gauge PVC [METHOD] conduit complete with all accessories and connected to fire alarm panel | No. |  |  |  | Fire Alarm Devices/Security Devices | BOQ-ELC-FireAlarm | BOQ-ELC-FireAlarm — Count | "Fire alarm " + if(FLS_SFTY_DEV_TYPE_TXT<>"",FLS_SFTY_DEV_TYPE_TXT,"detector") + " in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","20mm") + " PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"concealed") + " conduit complete with all accessories." | FLS_SFTY_DEV_TYPE_TXT, ELC_CDT_SZ_MM, ELC_CDT_INSTALL_METHOD_TXT | BOQ-ELC-FireAlarm |  | Detectors, MCPs, sounders, beacons separately.
4.4.2 | Addressable fire alarm control panel [ZONES] zones, [NR_LOOP] loops, complete with batteries, charger, printout, and all accessories | No. |  |  |  | Fire Alarm Devices/Security Devices | BOQ-ELC-FireAlarm | BOQ-ELC-FireAlarmPanel — Count | "Addressable FACP " + if(FLS_SFTY_DEV_TYPE_TXT<>"",FLS_SFTY_DEV_TYPE_TXT,"") + " complete with batteries and accessories." | FLS_SFTY_DEV_TYPE_TXT | BOQ-ELC-FireAlarm |  | 1 per building or fire zone.
4.4.3 | CCTV [TYPE] camera points in [CDT_SZ]mm heavy gauge PVC concealed conduit/trunking, [MFR], complete with mounting bracket and all accessories | No. |  |  |  | Fire Alarm Devices/Security Devices | BOQ-ELC-FireAlarm | BOQ-ELC-Security — Count (CCTV) | "CCTV " + if(SEC_DEV_TYPE_TXT<>"",SEC_DEV_TYPE_TXT,"dome camera") + " in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " PVC concealed conduit, " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"Hikvision or equal") + " complete with bracket and accessories." | SEC_DEV_TYPE_TXT, ELC_CDT_SZ_MM, ASS_MANUFACTURER_TXT | BOQ-ELC-Security |  | Group by camera type.
4.4.4 | Digital video recorder (DVR/NVR) [CHANNELS]-channel complete with hard drive, monitor, UPS, and all accessories | No. |  |  |  | Fire Alarm Devices/Security Devices | BOQ-ELC-FireAlarm | BOQ-ELC-Security — Count (DVR) | "if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"DVR/NVR ") + "complete with HDD, monitor, UPS and accessories." | ASS_DESCRIPTION_TXT | BOQ-ELC-Security
BILL No.5 — MECHANICAL INSTALLATIONS (PLUMBING & DRAINAGE)
Preamble: Provide all materials, install, connect, and set to work the following all as described in the Specifications and Drawings. Pipework to BS EN 806. Sanitary fittings vitreous china to BS3402. NWSC connection approval required. All drainage falls as drawings, not less than 1:40 for branches, 1:80 for mains.
5.1 SANITARY FITTINGS
5.1.1 | [MFR] WC pan [TYPE], [COLOUR] colour, vitreous china to BS3402, with [OUTLET] outlet, complete with close coupled cistern, soft close seat and cover, flush pipe, and all accessories | No. |  |  |  | Plumbing Fixtures | BOQ-PLM-SanitaryWC | BOQ-PLM-SanitaryWC — Count | "if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"Armitage Shanks or equal") + " WC pan " + if(ASS_MODEL_NR_TXT<>"",ASS_MODEL_NR_TXT,"") + ", " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"white vitreous china") + ", with close coupled cistern, soft close seat and cover, complete with all accessories." | ASS_MANUFACTURER_TXT, ASS_MODEL_NR_TXT, ASS_DESCRIPTION_TXT | BOQ-PLM-SanitaryWC |  | Group by type mark. Uganda: standard white colour.
5.1.2 | [DIM] vitreous china wash hand basin pedestal/countertop, [TAPS] tap holes, [FINISH] finish, waste and trap, complete with mixer tap and all accessories as [MFR] or equal approved | No. |  |  |  | Plumbing Fixtures | BOQ-PLM-SanitaryWC | BOQ-PLM-SanitaryWHB — Count | "if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"600mm WHB") + " wash hand basin, " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"Armitage Shanks or equal") + " complete with mixer tap, waste, trap and all accessories." | ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT | BOQ-PLM-SanitaryWHB
5.1.3 | [DIM]mm vitreous china urinal [TYPE] complete with automatic flushing cistern, waste and all accessories as [MFR] or equal approved | No. |  |  |  | Plumbing Fixtures | BOQ-PLM-SanitaryWC | BOQ-PLM-SanitaryUrinal — Count | "if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"Urinal") + " " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"or equal approved") + " complete with auto flushing cistern, waste and accessories." | ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT | BOQ-PLM-Urinals
5.1.4 | [LITRE]L stainless steel kitchen sink [BOWLS] bowl complete with drainer, mixer tap, P-trap and all accessories as [MFR] or equal approved | No. |  |  |  | Plumbing Fixtures | BOQ-PLM-SanitaryWC | BOQ-PLM-Sinks — Count | "if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"Kitchen sink") + " " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"or equal approved") + " complete with drainer, mixer tap, P-trap and accessories." | ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT | BOQ-PLM-Sinks
5.1.5 | [LITRE]L capacity [FUEL] storage water heater complete with thermostat, pressure relief valve, and all accessories as [MFR] or equal approved | No. |  |  |  | Plumbing Fixtures | BOQ-PLM-SanitaryWC | BOQ-PLM-WaterHeater — Count | "if(PLM_HOTWTR_CAPACITY_L<>"",PLM_HOTWTR_CAPACITY_L+"L ","") + if(PLM_HOTWTR_FUEL_TYPE_TXT<>"",PLM_HOTWTR_FUEL_TYPE_TXT+" ","electric ") + "water heater complete with PRV, thermostat and accessories as " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"approved manufacturer") + " or equal." | PLM_HOTWTR_CAPACITY_L, PLM_HOTWTR_FUEL_TYPE_TXT, ASS_MANUFACTURER_TXT | BOQ-PLM-WaterHeater
5.2 PIPEWORK — COLD & HOT WATER
5.2.1 | [SZ]mm dia. [MAT] [PN_RATING] cold water pipework including all fittings, brackets, and supports complete with pressure test | LM |  |  |  | Pipes/Pipe Accessories | BOQ-PLM-Pipework | BOQ-PLM-Pipework — Length (CW filter) | "if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + if(PLM_PPE_MAT_TXT<>"",PLM_PPE_MAT_TXT+" ","PPR ") + "cold water pipe " + if(PLM_PPE_PSR_RATING_BAR<>"",PLM_PPE_PSR_RATING_BAR+" bar rated ","") + "complete with fittings." | PLM_PPE_SZ_MM, PLM_PPE_MAT_TXT, PLM_PPE_PSR_RATING_BAR | BOQ-PLM-Pipework | PLM_VEL_MPS > 2.0 → [!VEL > 2.0] PLM_PSR_KPA < 150 or > 600 → [!PSR] | Group by size + material. NWSC supply 150–400 kPa.
5.2.2 | [SZ]mm dia. [MAT] [PN_RATING] hot water pipework including all fittings, insulation, brackets, and supports complete with pressure test | LM |  |  |  | Pipes/Pipe Accessories | BOQ-PLM-Pipework | BOQ-PLM-Pipework — Length (HW filter) | "if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + if(PLM_PPE_MAT_TXT<>"",PLM_PPE_MAT_TXT+" ","PPR ") + "hot water pipe " + if(PLM_PPE_PSR_RATING_BAR<>"",PLM_PPE_PSR_RATING_BAR+" bar rated ","") + "insulated, complete with fittings." | PLM_PPE_SZ_MM, PLM_PPE_MAT_TXT, PLM_PPE_PSR_RATING_BAR | BOQ-PLM-Pipework | PLM_PPE_FLW_LPS > 2.0 → [!FLOW > 2.0 L/s] | Uganda: PPR pipe PN20 for HW is standard.
5.2.3 | [SZ]mm gate / globe / ball valves [MAT] including all accessories | No. |  |  |  | Pipes/Pipe Accessories | BOQ-PLM-Pipework | BOQ-PLM-Valves — Count | "if(PLM_VLV_SZ_NR<>"",PLM_VLV_SZ_NR+"mm ","") + if(PLM_VLV_TYPE_TXT<>"",PLM_VLV_TYPE_TXT,"globe valve") + "." | PLM_VLV_SZ_NR, PLM_VLV_TYPE_TXT | BOQ-PLM-Valves |  | Group by size and type.
5.2.4 | [SZ]mm dia. [MAT] drainage pipework including all fittings, brackets, supports, and testing | LM |  |  |  | Pipes/Pipe Accessories | BOQ-PLM-Pipework | BOQ-PLM-Drainage — Length | "if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + if(PLM_DRN_BODY_MAT_TXT<>"",PLM_DRN_BODY_MAT_TXT+" ","uPVC ") + "drainage pipe complete with fittings." | PLM_PPE_SZ_MM, PLM_DRN_BODY_MAT_TXT | BOQ-PLM-Drainage |  | Min fall 1:40 branches, 1:80 mains.
5.2.5 | [SZ]mm dia. [MATERIAL] rainwater head / gully / inspection chamber / manhole [DEPTH] deep including frame, cover, benching and render | No. |  |  |  | Pipes/Pipe Accessories | BOQ-PLM-Pipework | BOQ-PLM-Drainage fittings — Count | "if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"drainage fitting") + "." | PLM_PPE_SZ_MM, ASS_DESCRIPTION_TXT | BOQ-PLM-Drainage
BILL No.6 — FIRE FIGHTING INSTALLATIONS
Preamble: Provide all materials, install, connect and set to work the following all as described in the Specifications and Drawings. All works to BS EN 12845 (sprinklers), BS 5306 (hose reels/extinguishers), Uganda NBC fire code. Uganda Fire & Rescue Services Authority approval required before commissioning.
6.1 PORTABLE FIRE EXTINGUISHERS
6.1.1 | [CAPACITY]kg [TYPE] fire extinguisher complete with wall bracket, signage, and commissioning as [MFR] or equal approved | No. |  |  |  | Sprinklers/Fire Protection | BOQ-FLS-Extinguishers | BOQ-FLS-Extinguishers — Count | "if(FLS_SFTY_DEV_TYPE_TXT<>"",FLS_SFTY_DEV_TYPE_TXT,"6kg ABC dry powder") + " fire extinguisher complete with bracket and signage." | FLS_SFTY_DEV_TYPE_TXT, ASS_MANUFACTURER_TXT | BOQ-FLS-Extinguishers |  | Uganda: minimum 1 per 200m². ABC type standard.
6.1.2 | [LITRE]L CO2 fire extinguisher for electrical panels complete with wall bracket, signage, and commissioning | No. |  |  |  | Sprinklers/Fire Protection | BOQ-FLS-Extinguishers | BOQ-FLS-Extinguishers — Count (CO2) | "if(FLS_SFTY_DEV_TYPE_TXT<>"",FLS_SFTY_DEV_TYPE_TXT,"2kg CO2") + " fire extinguisher for electrical areas complete with bracket and signage." | FLS_SFTY_DEV_TYPE_TXT | BOQ-FLS-Extinguishers |  | 1 per DB room minimum.
6.2 HOSE REELS
6.2.1 | [DIA]mm dia. [LENGTH]m [TYPE] hose reel complete with shut-off nozzle, semi-automatic valve, hose cabinet, and all connections | No. |  |  |  | Sprinklers | BOQ-FLS-HoseReels | BOQ-FLS-HoseReels — Count | "if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"25mm dia. 30m") + " hose reel, semi-automatic, complete with cabinet and connections." | ASS_DESCRIPTION_TXT, ASS_MANUFACTURER_TXT | BOQ-FLS-HoseReels |  | BS 5306 Part 1. Max 6 bar static pressure.
6.2.2 | [SZ]mm dia. [MAT] [PN] hose reel supply pipework including all fittings, valves, and supports complete with pressure test | LM |  |  |  | Sprinklers | BOQ-FLS-HoseReels | BOQ-FLS-HoseReels pipe — Length | "if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + if(PLM_PPE_MAT_TXT<>"",PLM_PPE_MAT_TXT+" ","black steel ") + "hose reel supply pipe complete with fittings and pressure test." | PLM_PPE_SZ_MM, PLM_PPE_MAT_TXT, PLM_PPE_PSR_RATING_BAR | BOQ-FLS-Pipework
6.3 SPRINKLER SYSTEM
6.3.1 | [TYPE] [COVERAGE] sprinkler head [ACTIVATION_TEMP]°C activation temperature including all accessories | No. |  |  |  | Sprinklers/Pipes | BOQ-FLS-Sprinklers | BOQ-FLS-Sprinklers — Count | "if(FLS_SPK_TYPE_TXT<>"",FLS_SPK_TYPE_TXT,"Concealed pendant") + " sprinkler head " + if(FLS_SPK_ACTIVATION_TEMP_C<>"",FLS_SPK_ACTIVATION_TEMP_C+"°C ","68°C ") + if(FLS_SPK_COVERAGE_M2<>"",FLS_SPK_COVERAGE_M2+"m² coverage ","") + "complete with accessories." | FLS_SPK_TYPE_TXT, FLS_SPK_ACTIVATION_TEMP_C, FLS_SPK_COVERAGE_M2 | BOQ-FLS-Sprinklers |  | BS EN 12845. Group by hazard classification.
6.3.2 | [SZ]mm dia. [MAT] [PN] sprinkler pipework distribution including all fittings, hangers, and supports | LM |  |  |  | Sprinklers/Pipes | BOQ-FLS-Sprinklers | BOQ-FLS-Pipework — Length | "if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + if(PLM_PPE_MAT_TXT<>"",PLM_PPE_MAT_TXT+" ","black steel ") + "sprinkler distribution pipe complete with fittings." | PLM_PPE_SZ_MM, PLM_PPE_MAT_TXT | BOQ-FLS-Pipework |  | Group by size.
6.3.3 | Sprinkler control valve set, zone control valve, test and drain valve, pressure gauges, alarm valve, and all accessories | No. |  |  |  | Sprinklers/Pipes | BOQ-FLS-Sprinklers | Manual | "Sprinkler control valve set complete with alarm valve, zone valves, drain, and pressure gauges." | ASS_DESCRIPTION_TXT | BOQ-FLS-ControlValves |  | 1 per sprinkler zone.
6.3.4 | Sprinkler pump set [FLOW]L/min at [PRESSURE]bar, electric duty/standby pumps with jockey pump, motor starters, and all accessories | No. |  |  |  | Sprinklers/Pipes | BOQ-FLS-Sprinklers | Manual | "Sprinkler pump set " + if(HVC_CAP_KW<>"",HVC_CAP_KW+"kW ","") + "complete with duty/standby pumps, jockey pump and starters." | HVC_CAP_KW, ASS_DESCRIPTION_TXT | BOQ-FLS-PumpSet |  | Manufacturer: Grundfos, Lowara or equal.
BILL No.7 — HVAC INSTALLATIONS
Preamble: Provide all materials, install, connect and set to work the following all as described in the Specifications and Drawings. All works to ASHRAE 90.1 tropical edition. Refrigerant pipework by certified F-Gas engineer. BMS interface points as Section 9. Uganda: NEMA refrigerant compliance.
7.1 VRF/VRV SPLIT SYSTEM EQUIPMENT
7.1.1 | [BRAND] VRF outdoor condensing unit(s) [CAPACITY]kW total cooling capacity, [REFRIGERANT] refrigerant, [PHASE]-phase [VLT]V power supply, including frame and vibration isolators | No. |  |  |  | Mechanical Equipment | BOQ-HVC-Equipment | BOQ-HVC-Equipment — Count (Outdoor) | "if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"VRF") + " outdoor condensing unit " + if(HVC_CAP_KW<>"",HVC_CAP_KW+"kW cooling, ","TBC kW, ") + if(HVC_REFRIGERANT_TXT<>"",HVC_REFRIGERANT_TXT+" refrigerant, ","R410A, ") + if(HVC_EFF_RATIO_NR<>"",HVC_EFF_RATIO_NR+" COP, ","") + if(HVC_PWR_KW<>"",HVC_PWR_KW+"kW power.","as drawings.") | ASS_MANUFACTURER_TXT, HVC_CAP_KW, HVC_REFRIGERANT_TXT, HVC_EFF_RATIO_NR, HVC_PWR_KW | BOQ-HVC-Equipment | HVC_CAP_KW — check per floor schedule HVC_EFF_RATIO_NR < 2.8 → [!COP LOW] | Group by system mark. Mitsubishi, Daikin, LG standard Uganda.
7.1.2 | [BRAND] VRF indoor [TYPE] unit [CAPACITY]kW cooling, [REFRIGERANT], including drain, controls, and all accessories | No. |  |  |  | Mechanical Equipment | BOQ-HVC-Equipment | BOQ-HVC-Equipment — Count (Indoor) | "if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"VRF") + " indoor " + if(HVC_UNIT_TYPE_TXT<>"",HVC_UNIT_TYPE_TXT,"cassette") + " unit " + if(HVC_CAP_KW<>"",HVC_CAP_KW+"kW cooling, ","TBC kW, ") + "complete with drain, remote control and accessories." | ASS_MANUFACTURER_TXT, HVC_CAP_KW, HVC_UNIT_TYPE_TXT | BOQ-HVC-Equipment | HVC_CAP_KW — verify per room design load | Group by indoor unit type.
7.1.3 | Split/package window/wall air conditioning unit [CAPACITY]kW cooling, [REFRIGERANT], [PHASE]-phase supply, complete with all accessories (non-VRF buildings) | No. |  |  |  | Mechanical Equipment | BOQ-HVC-Equipment | BOQ-HVC-Equipment — Count (Split) | "if(HVC_CAP_KW<>"",HVC_CAP_KW+"kW ","") + "split AC unit " + if(HVC_REFRIGERANT_TXT<>"",HVC_REFRIGERANT_TXT,"R410A") + " complete with all accessories." | HVC_CAP_KW, HVC_REFRIGERANT_TXT, HVC_EFF_RATIO_NR | BOQ-HVC-Equipment |  | For smaller buildings without VRF.
7.2 REFRIGERANT PIPEWORK
7.2.1 | [DIA]mm dia. refrigerant liquid/suction copper pipework insulated complete with all fittings and supports | LM |  |  |  | Pipes | BOQ-HVC-RefrigPipework | BOQ-HVC-RefrigPipework — Length | "if(PLM_PPE_SZ_MM<>"",PLM_PPE_SZ_MM+"mm ","") + "copper refrigerant " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"liquid/suction") + " pipe insulated, complete with fittings." | PLM_PPE_SZ_MM, ASS_DESCRIPTION_TXT | BOQ-HVC-RefrigPipework |  | By F-Gas certified engineer.
7.2.2 | Refrigerant branch distributor / Y-joint / header set including all fittings | No. |  |  |  | Pipes | BOQ-HVC-RefrigPipework | BOQ-HVC-RefrigFittings — Count | "Refrigerant " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"branch distributor") + " complete with all fittings." | ASS_DESCRIPTION_TXT | BOQ-HVC-RefrigFittings
7.3 DUCTWORK & DISTRIBUTION
7.3.1 | Galvanised mild steel [CLASS] rectangular ductwork [W]mm x [H]mm insulated [THICK]mm complete with all flanges, hangers, supports, and sealant | LM |  |  |  | Ducts/Flex Ducts/Air Terminals | BOQ-HVC-Ducts | BOQ-HVC-Ducts — Length | "GMS " + if(HVC_DUCT_CLASS_TXT<>"",HVC_DUCT_CLASS_TXT,"Class B") + " duct " + if(HVC_DCT_SZ_W_MM<>"",HVC_DCT_SZ_W_MM+"W","?W") + "x" + if(HVC_DCT_SZ_H_MM<>"",HVC_DCT_SZ_H_MM+"H mm ","?H mm ") + "insulated, complete with hangers." | HVC_DUCT_CLASS_TXT, HVC_DCT_SZ_W_MM, HVC_DCT_SZ_H_MM, HVC_DCT_LINING_TXT | BOQ-HVC-Ducts | HVC_VEL_MPS > 8.0 → [!VEL > 8.0 m/s] | Group by size. Uganda: GMS standard. Max vel 8m/s supply, 6m/s return.
7.3.2 | [DIA]mm dia. GMS circular ductwork insulated [THICK]mm complete with all fittings, hangers, and supports | LM |  |  |  | Ducts/Flex Ducts/Air Terminals | BOQ-HVC-Ducts | BOQ-HVC-Ducts — Length (circular) | "if(HVC_DCT_SZ_W_MM<>"",HVC_DCT_SZ_W_MM+"mm dia ","") + "GMS circular duct insulated complete with fittings." | HVC_DCT_SZ_W_MM | BOQ-HVC-Ducts | HVC_VEL_MPS > 8.0 → [!VEL]
7.3.3 | [DIA]mm dia. flexible duct [LENGTH]mm long connecting rigid duct to terminal complete with clamps | No. |  |  |  | Ducts/Flex Ducts/Air Terminals | BOQ-HVC-Ducts | BOQ-HVC-FlexDucts — Count | "if(HVC_DCT_FLEX_DIA_MM<>"",HVC_DCT_FLEX_DIA_MM+"mm dia ","") + "flexible duct " + if(HVC_DCT_FLEX_MAX_LEN_MM<>"",HVC_DCT_FLEX_MAX_LEN_MM+"mm long ","") + "complete with clamps." | HVC_DCT_FLEX_DIA_MM, HVC_DCT_FLEX_MAX_LEN_MM | BOQ-HVC-FlexDucts | HVC_DCT_FLEX_MAX_LEN_MM > 1500 → [!FLEX > 1500mm] | Max 1500mm per SMACNA. One per terminal.
7.3.4 | [TYPE] [SIZE]mm x [SIZE]mm supply/return air grille/diffuser/louvre complete with opposed blade damper and all accessories | No. |  |  |  | Ducts/Flex Ducts/Air Terminals | BOQ-HVC-Ducts | BOQ-HVC-AirTerminals — Count | "if(HVC_TERMINAL_TYPE_TXT<>"",HVC_TERMINAL_TYPE_TXT,"Supply grille") + " " + if(HVC_DCT_SZ_W_MM<>"",HVC_DCT_SZ_W_MM+"x","") + if(HVC_DCT_SZ_H_MM<>"",HVC_DCT_SZ_H_MM+"mm ","") + "complete with OBD and accessories." | HVC_TERMINAL_TYPE_TXT, HVC_DCT_SZ_W_MM, HVC_DCT_SZ_H_MM | BOQ-HVC-AirTerminals | HVC_DCT_TERMINAL_SOUND_DB_NR > 35 → [!NOISE] | Group by type and size.
BILL No.8 — LIFT INSTALLATIONS
Preamble: Provide and install [NR] lifts all as described in the Specifications and Drawings. All works to BS EN 81-20 and Uganda Government Lift Inspector requirements. Include all builder's works, pit ladder, machine room, and fireman's switch. KCCA/Government lift inspection certificate required before commissioning.
8.1 PASSENGER & GOODS LIFTS
8.1.1 | [BRAND] [CAPACITY]kg capacity [STOPS]-stop passenger lift, [SPEED]m/s, [DRIVE] drive, [FINISHES] car interior finish, complete with landing doors, controls, emergency phone, and all accessories as specification | No. |  |  |  | Specialty Equipment | BOQ-LIFT-Equipment | BOQ-LIFT-Equipment — Count | "if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"Otis/KONE or equal") + " " + if(ASS_CAPACITY_TXT<>"",ASS_CAPACITY_TXT,"1000kg") + " passenger lift, " + if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"") + " complete with all accessories and controls." | ASS_MANUFACTURER_TXT, ASS_CAPACITY_TXT, ASS_DESCRIPTION_TXT | BOQ-LIFT-Equipment |  | Uganda: 1000kg (13 person) standard. BS EN 81-20.
8.1.2 | Voltage stabiliser [KVA]kVA for lift power supply complete with all connections and accessories | No. |  |  |  | Specialty Equipment | BOQ-LIFT-Equipment | BOQ-LIFT-VoltageStabiliser — Count | "if(ASS_CAPACITY_TXT<>"",ASS_CAPACITY_TXT,"15kVA") + " voltage stabiliser for lift power supply complete with connections." | ASS_CAPACITY_TXT, ASS_DESCRIPTION_TXT | BOQ-LIFT-Equipment |  | Uganda: UMEME voltage fluctuation mitigation.
8.1.3 | Fireman's switch and emergency recall controls complete with all accessories | No. |  |  |  | Specialty Equipment | BOQ-LIFT-Equipment | BOQ-LIFT-Equipment | "Fireman's switch and emergency recall controls complete with accessories." | ASS_DESCRIPTION_TXT | BOQ-LIFT-Equipment |  | Required by Uganda NBC fire code.
8.1.4 | Builder's work in connection with lift installation including pit, shaft, machine room slab penetrations, fixings, and making good | Item |  |  |  | Specialty Equipment | BOQ-LIFT-Equipment | Manual | "Builder's work in connection with lift installation." | N/A | BOQ-LIFT-BuildersWork |  | Allow 5–8% of lift value.
8.1.5 | Government lift inspector initial commissioning inspection fee and certification | Item |  |  |  | Specialty Equipment | BOQ-LIFT-Equipment | Manual | "Government lift inspector commissioning fee." | N/A | BOQ-LIFT-Inspection |  | Uganda: Director of Industrial Training. Annual inspection thereafter.
BILL No.9 — ICT & SPECIALIST SYSTEMS
Preamble: Provide all materials, install, connect and set to work the following ICT, BMS, nurse call, and specialist systems all as described in the Specifications and Drawings. All structured cabling to TIA-568-C. BACnet/IP protocol for BMS. CCTV NVR/DVR 30-day retention minimum.
9.1 STRUCTURED DATA & VOICE CABLING
9.1.1 | Cat [RATING] data outlet points in [CDT_SZ]mm heavy gauge PVC [METHOD] conduit, [MFR] keystone jack, complete with faceplates and all accessories | No. |  |  |  | Data/Telephone Devices | BOQ-ICT-DataOutlets | BOQ-ICT-DataOutlets — Count | "Cat " + if(ICT_CAT_RATING_TXT<>"",ICT_CAT_RATING_TXT,"6") + " data outlet in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","25mm") + " PVC " + if(ELC_CDT_INSTALL_METHOD_TXT<>"",ELC_CDT_INSTALL_METHOD_TXT,"concealed") + " conduit, " + if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"Panduit or equal") + " complete with faceplate and accessories." | ICT_CAT_RATING_TXT, ELC_CDT_SZ_MM, ELC_CDT_INSTALL_METHOD_TXT, ASS_MANUFACTURER_TXT | BOQ-ICT-DataOutlets |  | TIA-568-C.2. Group by floor.
9.1.2 | Telephone outlet points in [CDT_SZ]mm heavy gauge PVC [METHOD] conduit complete with faceplate and all accessories | No. |  |  |  | Data/Telephone Devices | BOQ-ICT-DataOutlets | BOQ-ICT-DataOutlets — Count (Tel) | "Telephone outlet in " + if(ELC_CDT_SZ_MM<>"",ELC_CDT_SZ_MM+"mm","20mm") + " PVC conduit complete with faceplate." | ELC_CDT_SZ_MM, ICT_OUTLET_TYPE_TXT | BOQ-ICT-DataOutlets
9.1.3 | [NR]-port network patch panel Cat [RATING] in [U]-U rack including all patch leads and accessories | No. |  |  |  | Data/Telephone Devices | BOQ-ICT-DataOutlets | BOQ-ICT-PatchPanel — Count | "if(ICT_PORT_NR<>"",ICT_PORT_NR+"-port ","24-port ") + "patch panel Cat " + if(ICT_CAT_RATING_TXT<>"",ICT_CAT_RATING_TXT,"6") + " complete with patch leads." | ICT_PORT_NR, ICT_CAT_RATING_TXT, ICT_PATCH_PANEL_TXT | BOQ-ICT-PatchPanel
9.1.4 | [NR]-U network rack complete with PDU, cable management, blanking panels, and ventilated top panel | No. |  |  |  | Data/Telephone Devices | BOQ-ICT-DataOutlets | BOQ-ICT-Rack — Count | "if(ASS_DESCRIPTION_TXT<>"",ASS_DESCRIPTION_TXT,"19-inch") + " network rack complete with PDU, cable management and blanking." | ASS_DESCRIPTION_TXT | BOQ-ICT-Rack
9.2 BMS CONTROLS
9.2.1 | BMS [TYPE] controller [BACNET_ID], [PROTOCOL] protocol, [POINTS] I/O points, complete with power supply, housing, and all accessories | No. |  |  |  | Communication Devices | BOQ-ICT-BMS | BOQ-ICT-BMS — Count | "if(COM_C_DEV_TYPE_TXT<>"",COM_C_DEV_TYPE_TXT,"BMS controller") + " BACnet/IP, instance " + if(COM_C_DEV_BACNET_INSTANCE_INT<>"",COM_C_DEV_BACNET_INSTANCE_INT,"?") + " complete with I/O, power supply and housing." | COM_C_DEV_TYPE_TXT, COM_C_DEV_BACNET_INSTANCE_INT, COM_C_NETWORK_ADDRESS_TXT | BOQ-ICT-BMS |  | Vendor: Honeywell, Siemens, Schneider or equal.
9.2.2 | BMS field device [TYPE] sensor/actuator complete with wiring, mounting, and commissioning | No. |  |  |  | Communication Devices | BOQ-ICT-BMS | BOQ-ICT-BMS — Count (sensors) | "BMS " + if(COM_C_DEV_TYPE_TXT<>"",COM_C_DEV_TYPE_TXT,"sensor") + " complete with wiring and commissioning." | COM_C_DEV_TYPE_TXT, COM_C_MEAS_RANGE_TXT | BOQ-ICT-BMS
9.2.3 | BMS workstation software licence, operator interface, and commissioning complete as specified | Item |  |  |  | Communication Devices | BOQ-ICT-BMS | Manual | "BMS operator workstation, software licence and commissioning." | N/A | BOQ-ICT-BMS |  | 1 per project.
9.3 NURSE CALL SYSTEM (HEALTHCARE ONLY)
9.3.1 | Nurse call [TYPE] call point in ward/bed complete with pull cord, reset, zone indicator light, and all accessories connected to nurse call panel | No. |  |  |  | Nurse Call Devices | BOQ-ICT-NurseCall | BOQ-ICT-NurseCall — Count | "if(NCL_CALL_TYPE_TXT<>"",NCL_CALL_TYPE_TXT,"Nurse call point") + " zone " + if(NCL_ZONE_TXT<>"",NCL_ZONE_TXT,"?") + " complete with pull cord, indicator and accessories." | NCL_CALL_TYPE_TXT, NCL_ZONE_TXT, COM_C_PROTOCOL_TXT | BOQ-ICT-NurseCall |  | HTM 08-03. Healthcare projects only.
9.3.2 | Nurse call master control panel for [ZONES] zones complete with display, repeater panel, and all accessories | No. |  |  |  | Nurse Call Devices | BOQ-ICT-NurseCall | BOQ-ICT-NurseCall — Count (Panel) | "Nurse call master panel for " + if(NCL_ZONE_TXT<>"",NCL_ZONE_TXT,"?") + " zones complete with display and accessories." | NCL_ZONE_TXT | BOQ-ICT-NurseCall
9.4 GENERATOR & STANDBY POWER (WHERE APPLICABLE)
9.4.1 | [BRAND] [CAPACITY]kVA diesel generator set with canopy, [FUEL]L base tank, [PHASE]-phase, complete with all accessories, ATS panel, wiring, and commissioning | No. |  |  |  | Specialty Equipment | BOQ-ELEC-Generator | BOQ-ELEC-Generator — Count | "if(ASS_MANUFACTURER_TXT<>"",ASS_MANUFACTURER_TXT,"FG Wilson or equal") + " " + if(ASS_CAPACITY_TXT<>"",ASS_CAPACITY_TXT,"100kVA") + " diesel generator with canopy, base tank, ATS, complete with commissioning." | ASS_MANUFACTURER_TXT, ASS_CAPACITY_TXT, ASS_DESCRIPTION_TXT | BOQ-ELEC-Generator |  | Uganda: essential for all commercial/institutional buildings.
9.4.2 | Automatic Transfer Switch (ATS) panel [RATING]A for [PHASES]-phase mains/generator changeover complete with all accessories | No. |  |  |  | Specialty Equipment | BOQ-ELEC-Generator | BOQ-ELEC-ATS — Count | "ATS panel " + if(ELC_PNL_MAIN_BRK_A<>"",ELC_PNL_MAIN_BRK_A+"A ","?A ") + if(ELC_PNL_PHS_COUNT_NR<>"",ELC_PNL_PHS_COUNT_NR+"-phase ","") + "mains/generator changeover complete." | ELC_PNL_MAIN_BRK_A, ELC_PNL_PHS_COUNT_NR | BOQ-ELEC-ATS
REVIT SCHEDULE NAMES — Quick Reference
BOQ-STR-Foundations | Structural Foundations | Structural Foundations | Volume m³
BOQ-STR-Framing | Structural Framing / Beams / Columns | Structural Framing + Columns | Volume m³
BOQ-ARCH-Walling | Walls by type mark | Walls | Area m²
BOQ-ARCH-Ceilings | Ceilings by type mark | Ceilings | Area m²
BOQ-ARCH-FloorFinishes | Floors by type mark | Floors | Area m²
BOQ-ARCH-Roofing | Roofs by type mark | Roofs | Area m²
BOQ-ARCH-Doors | Doors by type mark | Doors | Count No.
BOQ-ARCH-Windows | Windows by type mark | Windows | Count No.
BOQ-ARCH-Stairs | Stairs | Stairs | Count No.
BOQ-ELC-Lighting-Points | Electrical Fixtures — lighting circuits | Electrical Fixtures | Count No.
BOQ-ELC-Socket-Points | Electrical Fixtures — socket circuits | Electrical Fixtures | Count No.
BOQ-ELC-Luminaires | Lighting Fixtures by type mark | Lighting Fixtures | Count No.
BOQ-ELC-Switches | Electrical Fixtures — switches | Electrical Fixtures | Count No.
BOQ-ELC-Sockets | Electrical Fixtures — sockets | Electrical Fixtures | Count No.
BOQ-ELC-Conduits | Conduits by size/material | Conduits | Length LM
BOQ-ELC-CableTrays | Cable Trays by size | Cable Trays | Length LM
BOQ-ELC-DBPanels | Electrical Equipment (panels) | Electrical Equipment | Count No.
BOQ-ELC-FireAlarm | Fire Alarm Devices by type | Fire Alarm Devices | Count No.
BOQ-ELC-Security | Security Devices by type | Security Devices | Count No.
BOQ-PLM-SanitaryWC | Plumbing Fixtures — WC | Plumbing Fixtures | Count No.
BOQ-PLM-SanitaryWHB | Plumbing Fixtures — WHB | Plumbing Fixtures | Count No.
BOQ-PLM-Pipework | Pipes by size/material | Pipes | Length LM
BOQ-PLM-Valves | Pipe Accessories — valves | Pipe Accessories | Count No.
BOQ-FLS-Extinguishers | Sprinklers (category) — extinguishers | Sprinklers | Count No.
BOQ-FLS-HoseReels | Sprinklers (category) — hose reels | Sprinklers | Count No.
BOQ-FLS-Sprinklers | Sprinklers by type | Sprinklers | Count No.
BOQ-HVC-Equipment | Mechanical Equipment by type mark | Mechanical Equipment | Count No.
BOQ-HVC-Ducts | Ducts by size | Ducts | Length LM
BOQ-HVC-FlexDucts | Flex Ducts | Flex Ducts | Count No.
BOQ-HVC-AirTerminals | Air Terminals by type | Air Terminals | Count No.
BOQ-LIFT-Equipment | Specialty Equipment — lifts | Specialty Equipment | Count No.
BOQ-ICT-DataOutlets | Data/Telephone Devices | Data/Telephone Devices | Count No.
BOQ-ICT-BMS | Communication Devices — BMS | Communication Devices | Count No.
BOQ-ICT-NurseCall | Nurse Call Devices | Nurse Call Devices | Count No.
BOQ-ELEC-Generator | Specialty Equipment — generator | Specialty Equipment | Count No.